## MCP_or_generator_list
Plant Name	NACE Code (required information)	Traceable identifier for the individual medium combustion plant (MCP) or generator (required information)	Plant Manufacturer	Model Name	Is the plant stationary or mobile?	Stack or emission point national grid reference (required information)	Easting	Northing	Latitude	Longitude	Date operation started (required information)	Rated thermal input of the individual MCP or generator in MW thermal (required information)	Total rated thermal input of all plant or generators on site in MWth	Technology or type (required information)	Main fuel type used (required information)	Secondary fuel type used (required information if plant is dual fired or uses a secondary fuel as a back up)	Is the secondary fuel used as a back up? and/or does the plant co fire using the secondary fuel?	Percentage of secondary fuel type used	Will the medium combustion plant be operated as a limited operting hours plant? (required information)	Annual operating hours. Please enter the hours the plant is intended to run.	Do you want to declare that your existing MCP will meet new MCP emission limit values (ELVs) from the medium combustion plant directive?	Annual load factor as a percentage	Background nitrogen dioxide (NO2) in ug/m3	Stack height (meters)	What is the emission rate for the pollutants (Nm3/s )	Is the plant in an Air Quality Management Area (AQMA) for a declared pollutant?	What is the name of the local authority who has declared th AQMA?	Closest human receptor (meters)	Human receptor details	Closest Ecological receptor (meters)	Ecological receptor details	Will secondary abatement be fitted to the plant	What type of secondary abatement will be fitted?	date of capacity market of balancing service agreement or FiT accreditation (DD/MM/YYYY)
Guidance	NACE code means Nomenclature of Economic Activities and is the European statistical classification of economic activities	Serial number or other unique identifier, name plate, manufacturer and or model				Enter the coordinates of the emission point of the plant (not the site). You should enter this as a National Grid Reference or as a Latitude and Longitude pair. You should enter the values using the same coordinate system that you collected the raw data in.					When the plant or generator was first put into operation or the commissioning date, leave blank if new and not yet operating	This is for each individual unit. You should calculate this using one of the methods in the Association of Manufacturers and suppliers of Power Systems and ancillary equipment (AMPS) technical note: "Determination of thermal input power of an engine driven generator".	This should be the total of all the individual units of any size	Boiler, Engine, Back up generator, turbine, boiler CHP, Engine CHP	Gas oil, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels	Gas oil, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels	Back up, co firing, both	Only required where co firing	Where the option of exemption under Article 6 (8) of the medium combustion plant directive is used the operator (as identified in Part A of the application form) can declare by indicating here that the MCP will not be operaterated more than the number of hours referred to in this paragraph.	This should be the total for the year and be to the nearest whole number	Applicable for existing MCP plant only. You may want to claim this to demonstrate low risk impacts to habitats as part of an air emissions risk assessment. If you do make this voluntary declaration we will include new MCP ELVs from the medium combustion plant directive in your permit.		Go to the Defra UK Air website and select the most recent background map data. Set the local authority to that of your site location and the pollutant to NO2			AQMAs interactive map								applicable to SG applications only
	Full Classification											Microsoft Word - AMPS8704 - AMPS Technical Committee document template update 03.docx (environment-agency.gov.uk)											Background Mapping data for local authorities - Defra, UK
	Simple List
Plant 1	C.11.05	GEN1234DE0001	Cummins	C12 D6T	stationary	ST 58132 72695			51.45168	-2.6039127	23/05/2016	2.1	12.4	Engine	Gas oil	natural gas	co firing	20	yes	7000	yes	90%	12	3		yes	Cheshire West and Chester	100	school	500	SSSI, SAC	Yes	SCR	01/12/2018
1B_C1_1	J.63.11	GEN-01-C1/1	MTU	DS3600	Stationary		550897.48	185314.48				7.6	174.8	Back up generator	Liquid fuels other than gas oil	Gas oil	Back up		yes	499		100%	16.24µg/m3 - maximum 2024 annual mean NO2 concentration from the 1km grid squares which cover the plant	20.6	2.46 (at 5% O2)	Yes	Barking and Dagenham London Borough Council	Adjacent	Commercial	30	LNR, LWS	Yes	SCR	n/a
1B_C1_2		GEN-01-C1/2	MTU	DS3600	Stationary		550904.73	185316.61				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C1_3		GEN-01-C1/3	MTU	DS3600	Stationary		550909.32	185318				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C4_1		GEN-01-C4/1	MTU	DS3600	Stationary		550916.37	185320.14				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C4_2		GEN-01-C4/2	MTU	DS3600	Stationary		550921.17	185321.52				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C4_3		GEN-01-C4/3	MTU	DS3600	Stationary		550928.32	185323.76				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C4_4		GEN-01-C2/1	MTU	DS3600	Stationary		550970.48	185336.57				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C2_1		GEN-01-C2/2	MTU	DS3600	Stationary		550976.14	185338.49				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C2_2		GEN-01-C2/3	MTU	DS3600	Stationary		550981.9	185340.2				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C2_3		GEN-01-C2/4	MTU	DS3600	Stationary		550987.77	185341.91				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C2_4		GEN-01-C5/1	MTU	DS3600	Stationary		550993.86	185343.83				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C5_1		GEN-01-C5/2	MTU	DS3600	Stationary		550999.73	185345.65				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C5_2		GEN-01-C5/3	MTU	DS3600	Stationary		551005.49	185347.67				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C5_3		GEN-01-C5/4	MTU	DS3600	Stationary		551011.36	185349.38				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C3_1		GEN-01-C3/1	MTU	DS3600	Stationary		551042.32	185358.45				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C3_2		GEN-01-C3/2	MTU	DS3600	Stationary		551048.19	185360.37				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C3_3		GEN-01-C3/3	MTU	DS3600	Stationary		551054.06	185362.4				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C3_4		GEN-01-C3/4	MTU	DS3600	Stationary		551059.82	185364.22				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C6_1		GEN-01-C6/1	MTU	DS3600	Stationary		551065.91	185365.82				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C6_2		GEN-01-C6/2	MTU	DS3600	Stationary		551071.99	185367.63				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C6_3		GEN-01-C6/3	MTU	DS3600	Stationary		551077.33	185369.45				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_C6_4		GEN-01-C6/4	MTU	DS3600	Stationary		551084.16	185371.26				7.6		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	2.46 (at 5% O2)	Yes						Yes	SCR
1B_H1		GEN-01-HA	MTU	DS1650	Stationary		550886.48	185312.13				3.8		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	3.43 (at 15% O2)	Yes						Yes	SCR
1B_H2		GEN-01-HB	MTU	DS1650	Stationary		550892.03	185313.95				3.8		Back up generator	Liquid fuels other than gas oil	Gas oil	Back up			499		100%		20.6	3.43 (at 15% O2)	Yes						Yes	SCR

## Resp_1
Plant Name	_1136	_1333	_1234	Easting	Northing	Lat	Long	_1224	_1137	_1118	_1125	_1152	_1230	_1138	_1328	_1062	_1326	_1021	_1015	_1140	_1121	_1117	_1124	_2005	_1016	_2006	_1150	_1040	_1225	_2017	Release Point NGR	Mobile Plant	NACE Code
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!
#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	#REF!	No	#REF!

Named Range	Value							MCP-DateCommissioned	ThermalInput	MCP-CombustionTechnology	MCP-FuelMain	MCP-FuelSec	MCP-FuelSecWhen	MCP-FuelUsageSec	MCP-Limitedhrs		MeetnewELV	MCP-Loadas%	MCP-BackgroundNO2	MCP-StackHeight	AQMA	AQMA LA	HumanReceptor	MCP_HumanReceptorDetails	EcoReceptor	MCP_EcoReceptorDetails	MCP-Abated	MCP-AbateType	MCP-CapBalAgree
MobilePlant	No
NaceCode	#REF!

Plant Name	Plant Name
_1136	Serial No. of Plant / (If already purchased)
_1333	Plant Manufacturer
_1234	Model Name
Easting	Easting
Northing	Northing
Lat	Lat
Long	Long
_1224	Commissioning Date
_1137	Size (MWth)
_1118	Technology
_1125	Fuel/Main Fuel
IF an individual plant uses more than one fuel, give the proportions	IF an individual plant uses more than one fuel, give the proportions
0	0
02	0
03	0
04	0
Stack Height (metres)	Stack Height (metres)
_1027	If new plant does the flue share a common windshield?
_1062	Annual Hours
_1328	Limited Operating Hours
_1021	Annual Load (%)
_1121	In AQMA
_1117	AQMA Local Authority
_1124	Closest Human Receptor (metres)
_2005	Human Receptor Details
_1016	Closest Ecological Receptor (metres)
_2006	Ecological Receptor Details
_1015	Background NO2 (μg/m3)
_1150	Will secondary abatement be fitted to the plant?
_1040	Abatement Type
_1326	Will Meet New ELVs