## Ave Calc. 2025
Average Discharge levels | Units | 2024-11-18 | 2025-02-04 | 2025-04-07 | 2025-05-02 | 2025-06-09 | 2025-07-28 | 2025-08-28 | 2025-10-23 | 2025-10-23 | 2025-11-21 | Mean | Max
Ammonia total load | kg/d N | 1.782 | 3.18 | 0.6916 | 0.4563 |  |  | 0.1611 | 0.247 |  | 0.4616 | 0.99709 | 3.18
Ammonium total | mg/l N | 162 | 318 | 53.2 | 50.7 | 33.7 | 104 | 17.9 | 49.4 | 95.2 | 57.7 | 94.18 | 318
BOD (ATU) total load | kg/d O | [10 empty] | #DIV/0! | 0
BOD 5d total + ATU | mg/l O | [10 empty] | #DIV/0! | 0
Chromium total | µg/l Cr | [10 empty] | #DIV/0! | 0
Chromium total load | kg/d Cr | [10 empty] | #DIV/0! | 0
COD settled | mg/l O | 198 | 159 | 59 | 159 | 127 | 252 | 128 | 94 | 173 | 156 | 150.5 | 252
COD settled load | kg/d O | 2.178 | 1.59 | 0.767 | 1.431 |  |  | 1.152 | 0.47 |  | 1.248 | 1.2623 | 2.178
COD total | mg/l O | [10 empty] | #DIV/0! | 0
COD total load | kg/d O | [10 empty] | #DIV/0! | 0
COD/BOD ratio-total | none | [10 empty] | #DIV/0! | 0
Copper total | mg/l Cu | 0.033 | 0.557 | 0.033 | 0.062 | 0.026 | 0.088 | 0.303 | 0.067 | 0.08 | 0.026 | 0.1275 | 0.557
Copper total load | kg/d Cu | 0.0004 | 0.0056 | 0.0004 | 0.0006 |  |  | 0.0027 | 0.0003 |  |  | 0.0016667 | 0.0056
Cyanide free | mg/l CN | [5 empty] | 0.014 |  |  | 0.014 |  | 0.014 | 0.014
Day of week (1=Sun) | none | [10 empty] | #DIV/0! | 0
Flow total daily | m³/d | 11 | 10 | 13 | 9 | 14 | 9 | 9 | 5 |  | 8 | 9.7778 | 14
Flow instantaneous | l/s | [5 empty] | 0.26 |  |  | 0.2 |  | 0.23 | 0.26
Lead total | µg/l Pb | [10 empty] | #DIV/0! | 0
Nickel total | mg/l Ni | 2.32 | 22.5 | 0.263 | 0.512 | 0.368 | 0.394 | 10.8 | 2.11 | 2.01 | 0.533 | 4.181 | 22.5
Nickel total load | kg/d Ni | 0.0255 | 0.225 | 0.0034 | 0.0046 |  |  | 0.0972 | 0.0106 |  | 0.0043 | 0.052943 | 0.225
Non settleable solids | mg/l | 34 | 62 | 15 | 14 | 9.6 | 26 | 256 | 56 | 100 | 16 | 58.86 | 256
Sett. solids tot load | kg/d | 0.022 | 0.24 | 0.026 | 0.09 |  |  | 0.684 | 0.44 |  | 0.096 | 0.22829 | 0.684
Settleable solids | mg/l | 2 | 24 | 2 | 10 | 12 | 2 | 76 | 88 | 32 | 12 | 26 | 88
Solids part. 105°C | mg/l | [10 empty] | #DIV/0! | 0
Solids tot neut. load | kg/d | 0.396 | 0.86 | 0.221 | 0.216 |  |  | 2.988 | 0.72 |  | 0.224 | 0.80357 | 2.988
Susp. solids tot load | kg/d | [10 empty] | #DIV/0! | 0
Suspended solids pH 7 | mg/l | 36 | 86 | 17 | 24 | 12 | 28 | 332 | 144 | 132 | 28 | 83.9 | 332
Zinc total | mg/l Zn | [5 empty] | 0.07 |  |  | 0.07 |  | 0.07 | 0.07
Zinc total load | kg/d Zn | [10 empty] | #DIV/0! | 0
pH | pH units | [10 empty] | #DIV/0! | 0
pH (field measured) | pH units | [10 empty] | #DIV/0! | 0

## Ave Calc. 2023-24
Average Discharge levels | Units | 2023-12-06 | 2023-10-23 | 2023-12-07 | 2023-09-19 | 2023-08-31 | 2024-09-11 | 2024-07-29 | 2024-06-11 | 2024-04-16 | 2024-03-26 | 2024-02-27 | Mean | Max
Ammonia total load | kg/d N | 0.1602 | 0.978 | 73.5 |  | 0.7576 | 0.333 | 2.684 | 1.28 | 0.47 | 0.783 | 0.8 | 8.1746 | 73.5
Ammonium total | mg/l N | 53.4 | 163 |  | 163 | 94.7 | 111 | 244 | 160 | 235 | 163 | 160 | 154.71 | 244
BOD (ATU) total load | kg/d O | 0.513 | [10 empty] | 0.513 | 0.513
BOD 5d total + ATU | mg/l O | 171 | [10 empty] | 171 | 171
Chromium total | µg/l Cr | 23 |  |  |  | 26 |  |  |  | 23 |  |  | 24 | 26
Chromium total load | kg/d Cr |  |  |  |  | 0.0002 | [6 empty] | 0.0002 | 0.0002
COD settled | mg/l O | 402 | 309 | 482 | 1720 | 126 | 136 | 278 | 375 | 255 | 373 | 193 | 422.6364 | 1720
COD settled load | kg/d O | 1.206 | 1.854 |  |  | 1.008 | 0.408 | 3.058 | 3 | 0.51 | 1.119 | 0.965 | 1.4587 | 3.058
COD total | mg/l O | 421 | [10 empty] | 421 | 421
COD total load | kg/d O | 1.263 | [10 empty] | 1.263 | 1.263
COD/BOD ratio-total | none | 2.462 | [7 empty] | 0.048 |  |  | 1.255 | 2.462
Copper total | mg/l Cu | 0.19 | 0.108 | 0.078 | 0.342 | 0.112 | 0.156 | 0.099 | 0.067 | 0.0001 | 0.094 | 0.043 | 0.11719 | 0.342
Copper total load | kg/d Cu | 0.0006 | 0.0007 |  |  | 0.0009 | 0.0005 | 0.0011 | 0.0005 |  | 0.0003 | 0.0002 | 0.0006 | 0.0011
Cyanide free | mg/l CN |  |  |  | 0.008 | [7 empty] | 0.008 | 0.008
Day of week (1=Sun) | none | 4 | 2 | [9 empty] | 3 | 4
Flow total daily | m³/d | 3 | 6 |  |  | 8 | 3 | 11 | 8 | 2 | 3 | 5 | 5.4444 | 11
Flow instantaneous | l/s |  |  | 0.08 | 0.07 | [7 empty] | 0.075 | 0.08
Lead total | µg/l Pb | 290 |  |  |  | 290 |  |  |  | 290 |  |  | 290 | 290
Nickel total | mg/l Ni | 2 | 1.39 | 1.16 | 3.3 | 1.77 | 1.21 | 0.375 | 0.395 | 0.469 | 1.68 | 1.21 | 1.3599 | 3.3
Nickel total load | kg/d Ni | 0.006 | 0.0083 |  |  | 0.0142 | 0.0036 | 0.0041 | 0.0032 | 0.0009 | 0.005 | 0.0061 | 0.0057111 | 0.0142
Non settleable solids | mg/l | 32 | 28 | 22 | 98 | 52 | 16 | 48 | 18 | 186 | 118 | 38 | 59.6364 | 186
Sett. solids tot load | kg/d | 0.288 |  |  |  | 0.512 | 0.168 |  | 0.032 | 0.108 | 0.27 | 0.42 | 0.25686 | 0.512
Settleable solids | mg/l | 96 | 56 | 1 | 6 | 64 | 56 | 1 | 4 | 54 | 90 | 84 | 46.5455 | 96
Solids part. 105°C | mg/l | 234 | [10 empty] | 234 | 234
Solids tot neut. load | kg/d | 0.384 | 0.504 |  |  | 0.928 | 0.216 |  | 0.176 | 0.48 | 0.624 | 0.61 | 0.49025 | 0.928
Susp. solids tot load | kg/d | 0.702 | 0.336 | [9 empty] | 0.519 | 0.702
Suspended solids pH 7 | mg/l | 128 | 84 | 20 | 104 | 116 | 72 | 48 | 22 | 240 | 208 | 122 | 105.8182 | 240
Zinc total | mg/l Zn | 0.07 |  | 0.07 | 0.25 | 0.09 |  |  |  | 0.07 |  |  | 0.11 | 0.25
Zinc total load | kg/d Zn |  |  |  |  | 0.0007 | [6 empty] | 0.0007 | 0.0007
pH | pH units |  |  |  | 7.4 | [7 empty] | 7.4 | 7.4
pH (field measured) | pH units |  |  |  | 7 | [7 empty] | 7 | 7

## Raw Data 2023-24
Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance
Ammonia total load | kg/d N | 0.8 | - |  | Ammonia total load | kg/d N | 0.783 | - |  | Ammonia total load | kg/d N | 0.47 | - |  | Ammonia total load | kg/d N | 1.28 | - |  | Ammonia total load | kg/d N | 2.684 | - |  | Ammonia total load | kg/d N | 0.333 | -
Ammonium total | mg/l N | 160 | - |  | Ammonium total | mg/l N | 261 | - |  | Ammonium total | mg/l N | 235 | - |  | Ammonium total | mg/l N | 160 | - |  | Ammonium total | mg/l N | 244 | - |  | Ammonium total | mg/l N | 111 | -
COD settled | mg/l O | 193 | 3000 | Pass | COD settled | mg/l O | 373 | 3000 | Pass | Chromium total | µg/l Cr | 23 | - |  | COD settled | mg/l O | 375 | 3000 | Pass | COD settled | mg/l O | 278 | 3000 | Pass | COD settled | mg/l O | 136 | 3000 | Pass
COD settled load | kg/d O | 0.965 | - |  | COD settled load | kg/d O | 1.119 | - |  | COD settled | mg/l O | 255 | 3000 | Pass | COD settled load | kg/d O | 3 | - |  | COD settled load | kg/d O | 3.058 | - |  | COD settled load | kg/d O | 0.408 | -
Copper total | mg/l Cu | 0.043 | 1 | Pass | Copper total | mg/l Cu | 0.094 | 1 | Pass | COD settled load | kg/d O | 0.51 | - |  | Copper total | mg/l Cu | 0.067 | 1 | Pass | Copper total | mg/l Cu | 0.099 | 1 | Pass | Copper total | mg/l Cu | 0.156 | 1 | Pass
Copper total load | kg/d Cu | 0.0002 | 0.015 | Pass | Copper total load | kg/d Cu | 0.0003 | 0.015 | Pass | Copper total | mg/l Cu | 0.048 | 1 | Pass | Copper total load | kg/d Cu | 0.0005 | 0.015 | Pass | Copper total load | kg/d Cu | 0.0011 | 0.015 | Pass | Copper total load | kg/d Cu | 0.0005 | 0.015 | Pass
Flow total daily | m³/d | 5 | - |  | Flow total daily | m³/d | 3 | - |  | Copper total load | kg/d Cu | 0.0001 | 0.015 | Pass | Flow total daily | m³/d | 8 | - |  | Flow total daily | m³/d | 11 | - |  | Flow total daily | m³/d | 3 | -
Nickel total | mg/l Ni | 1.21 | 4 | Pass | Nickel total | mg/l Ni | 1.68 | 4 | Pass | Flow total daily | m³/d | 2 | - |  | Nickel total | mg/l Ni | 0.395 | 4 | Pass | Nickel total | mg/l Ni | 0.375 | 4 | Pass | Nickel total | mg/l Ni | 1.21 | 4 | Pass
Nickel total load | kg/d Ni | 0.0061 | 0.06 | Pass | Nickel total load | kg/d Ni | 0.005 | 0.06 | Pass | Lead total | µg/l Pb | 290 | - |  | Nickel total load | kg/d Ni | 0.0032 | 0.06 | Pass | Nickel total load | kg/d Ni | 0.0041 | 0.06 | Pass | Nickel total load | kg/d Ni | 0.0036 | 0.06 | Pass
Non settleable solids | mg/l | 38 | - |  | Non settleable solids | mg/l | 118 | - |  | Nickel total | mg/l Ni | 0.469 | 4 | Pass | Non settleable solids | mg/l | 18 | - |  | Non settleable solids | mg/l | 48 | - |  | Non settleable solids | mg/l | 16 | -
Sett. solids tot load | kg/d | 0.42 | - |  | Sett. solids tot load | kg/d | 0.27 | - |  | Nickel total load | kg/d Ni | 0.0009 | 0.06 | Pass | Sett. solids tot load | kg/d | 0.032 | - |  | Settleable solids | mg/l | 1 | 250 | Pass | Sett. solids tot load | kg/d | 0.168 | -
Settleable solids | mg/l | 84 | 250 | Pass | Settleable solids | mg/l | 90 | 250 | Pass | Non settleable solids | mg/l | 186 | - |  | Settleable solids | mg/l | 4 | 250 | Pass | Suspended solids pH 7 | mg/l | 48 | - |  | Settleable solids | mg/l | 56 | 250 | Pass
Solids tot neut. load | kg/d | 0.61 | - |  | Solids tot neut. load | kg/d | 0.624 | - |  | Sett. solids tot load | kg/d | 0.108 | - |  | Solids tot neut. load | kg/d | 0.176 | - |  | 2024-07-29 |  |  |  |  | Solids tot neut. load | kg/d | 0.216 | -
Suspended solids pH 7 | mg/l | 122 | - |  | Suspended solids pH 7 | mg/l | 208 | - |  | Settleable solids | mg/l | 54 | 250 | Pass | Suspended solids pH 7 | mg/l | 22 | - | [6 empty] | Suspended solids pH 7 | mg/l | 72 | -
2024-02-27 |  |  |  |  | 2024-03-26 |  |  |  |  | Solids tot neut. load | kg/d | 0.48 | - |  | 2024-06-11 | [9 empty] | 2024-09-11
[10 empty] | Suspended solids pH 7 | mg/l | 240 | -
Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Zinc total | mg/l Zn | 0.07 | 1 | Pass
Ammonium total | mg/l N | 73.5 | - |  | Ammonia total load | kg/d N | 0.1602 | - |  | 2024-04-16
COD settled | mg/l O | 482 | 3000 | Pass | Ammonium total | mg/l N | 53.4 | - |  | eterminand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance | Determinand | Units | Value | Consent Limit | Compliance
Copper total | mg/l Cu | 0.078 | 1 | Pass | BOD (ATU) total load | kg/d O | 0.513 | - |  | Ammonia total load | kg/d N | 0.978 | - |  | Ammonium total | mg/l N | 163 | - |  | Ammonia total load | kg/d N | 0.7576 | -
Flow instantaneous | l/s | 0.08 | 0.4 | Pass | BOD 5d total + ATU | mg/l O | 171 | - |  | Ammonium total | mg/l N | 163 | - |  | COD settled | mg/l O | 1720 | 3000 | Pass | Ammonium total | mg/l N | 94.7 | -
Nickel total | mg/l Ni | 1.16 | 4 | Pass | Chromium total | µg/l Cr | 23 | - |  | COD settled | mg/l O | 309 | 3000 | Pass | Copper total | mg/l Cu | 0.342 | 1 | Pass | Chromium total | µg/l Cr | 26 | -
Non settleable solids | mg/l | 22 | - |  | COD settled | mg/l O | 402 | 3000 | Pass | COD settled load | kg/d O | 1.854 | - |  | Cyanide free | mg/l CN | 0.008 | 2 | Pass | Chromium total load | kg/d Cr | 0.0002 | -
Settleable solids | mg/l | 1 | 250 | Pass | COD settled load | kg/d O | 1.206 | - |  | Copper total | mg/l Cu | 0.108 | 1 | Pass | Flow instantaneous | l/s | 0.07 | 0.4 | Pass | COD settled | mg/l O | 126 | 3000 | Pass
Suspended solids pH 7 | mg/l | 20 | - |  | COD total | mg/l O | 421 | - |  | Copper total load | kg/d Cu | 0.0007 | 0.015 | Pass | Nickel total | mg/l Ni | 3.3 | 4 | Pass | COD settled load | kg/d O | 1.008 | -
Zinc total | mg/l Zn | 0.07 | 1 | Pass | COD total load | kg/d O | 1.263 | - |  | Day of week (1=Sun) | none | 2 | - |  | Non settleable solids | mg/l | 98 | - |  | Copper total | mg/l Cu | 0.112 | 1 | Pass
2023-12-07 |  |  |  |  | COD/BOD ratio-total | none | 2.462 | - |  | Flow total daily | m³/d | 6 | - |  | pH | pH units | 7.4 | 6 TO 10.5 | Pass | Copper total load | kg/d Cu | 0.0009 | 0.015 | Pass
[5 empty] | Copper total | mg/l Cu | 0.19 | 1 | Pass | Nickel total | mg/l Ni | 1.39 | 4 | Pass | pH (field measured) | pH units | 7 | 6 TO 10.5 | Pass | Flow total daily | m³/d | 8 | -
[5 empty] | Copper total load | kg/d Cu | 0.0006 | 0.015 | Pass | Nickel total load | kg/d Ni | 0.0083 | 0.06 | Pass | Settleable solids | mg/l | 6 | 250 | Pass | Lead total | µg/l Pb | 290 | -
[5 empty] | Day of week (1=Sun) | none | 4 | - |  | Non settleable solids | mg/l | 28 | - |  | Suspended solids pH 7 | mg/l | 104 | - |  | Nickel total | mg/l Ni | 1.77 | 4 | Pass
[5 empty] | Flow total daily | m³/d | 3 | - |  | Sett. solids tot load | kg/d | 0.336 | - |  | Zinc total | mg/l Zn | 0.25 | 1 | Pass | Nickel total load | kg/d Ni | 0.0142 | 0.06 | Pass
[5 empty] | Lead total | µg/l Pb | 290 | - |  | Settleable solids | mg/l | 56 | 250 | Pass | 2023-09-19 |  |  |  |  | Non settleable solids | mg/l | 52 | -
[5 empty] | Nickel total | mg/l Ni | 2 | 4 | Pass | Solids tot neut. load | kg/d | 0.504 | - | [6 empty] | Sett. solids tot load | kg/d | 0.512 | -
[5 empty] | Nickel total load | kg/d Ni | 0.006 | 0.06 | Pass | Suspended solids pH 7 | mg/l | 84 | - | [6 empty] | Settleable solids | mg/l | 64 | 250 | Pass
[5 empty] | Non settleable solids | mg/l | 32 | - |  | 2023-10-23 | [9 empty] | Solids tot neut. load | kg/d | 0.928 | -
[5 empty] | Sett. solids tot load | kg/d | 0.288 | - | [11 empty] | Suspended solids pH 7 | mg/l | 116 | -
[5 empty] | Settleable solids | mg/l | 96 | 250 | Pass | [10 empty] | Zinc total | mg/l Zn | 0.09 | 1 | Pass
[5 empty] | Solids part. 105°C | mg/l | 234 | - | [11 empty] | Zinc total load | kg/d Zn | 0.0007 | -
[5 empty] | Solids tot neut. load | kg/d | 0.384 | - | [11 empty] | 2023-08-31
[5 empty] | Susp. solids tot load | kg/d | 0.702 | -
[5 empty] | Suspended solids pH 7 | mg/l | 128 | -
[5 empty] | Zinc total | mg/l Zn | 0.07 | 1 | Pass
2023-12-06