Stripper Line – Chemically stripping nickel from plated parts.

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Tradebe

11 01 98

Stripper tank 2

Stripper tank 1

800L

800L

Demin water

METEX DEKOTE EN Concentrate – 500ml/L

METEX DEKOTE Base Salt – 120g/L

60g/L Uni-Clean 252

Microetch -66 60g/l

Sulphuric Acid (96%) 8.7L

Nitric Acid (60%)

Alumon AC-70 90g/l

Demin water

Line 1 – Medium Phosphorous Nickel plating line, including pretreatments (cleaners and acid etch) as well as

The electroless Nickel plating process and associated rinse tanks.

NIKLAD ELV 849M

NIKLAD ELV 849 HPH

NIKLAD 849 C5

Demin water

Nickel Chloride 240g/l

Hydrochloric Acid (30%)

Metex PS

Minco

Demin water

Hot Water rinse

22

Water rinse x2

21+20

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Tradebe

11 01 11 / 11 01 98

Tradebe

11 01 11 / 11 01 98 / 11 01 05

Bondal (ARP 303 ZN)            10

Elnic 101-RP2 (L)

Elnic 101-RP2  Elnic R-101 C5

Demin water

Tank volumes:1 is 1090L                                            18 is 890L

2,3,4,5,6, 7, 8, 9, 10, 11, 13,14, 15, 20 and 21 are 550L

16, 17, 18 are 675L

(540L)

Water Rinse2

Example route for Mild Steel: Uni-Clean 252, 10 minutes, Water Rinse 2/3, Hydrochloric Acid, 30 secs/1 minute, Water Rinse 14/15, Nickel Solution, Water Rinse 20/21, Hot Water Rinse.

Example route for Aluminium: Minco, 10 minutes, Water Rinse 5, White Etch, 20/30 secs, Water Rinse 8, Micro Etch, 30 secs, Water Rinse 8, Bondal, 45 secs, Water Rinse 11, Micro Etch, 20 secs, Water Rinse 8, Bondal, 30 secs, Water Rinse 11, Nickel Solution, Water Rinse 20/21, Hot Water Rinse.

HCL (15%)

12

Old White Etch

7

7

Effluent System

Effluent System

Effluent System

Nickel Solution

16

Demin water

Demin water

Demin water

Demin water

ARP 303 ZN (33%)

Demin water

Water rinse

15

Nickel PTFE

19

Nickel Solution

18

Nickel Solution

17

Water rinse

14

Nickel Strike

13

Water Rinse

11

Micro Etch

9

Water Rinse

8

White Etch

6

Water Rinse

5

Minco

4

Water Rinse

3

Uni-Clean 252

1  (1090L)

Line 2 – High Phosphorous Nickel plating line, including pretreatments (cleaners and acid etch) as well as

The electroless Nickel plating process and associated rinse tanks.

Demin water

60g/L Uni-Clean 252

Empty tank

7   (3600L)

Nickel Solution

6   (4700L)

Nickel Solution

5   (4700L)

Nickel Solution

4   (4700L)

Empty tank

3   (4000L)

Uni-Clean 252

2  (4000L)

Rinse

1   (4000L)

VandAloy 4100 A

VandAloy 4100 B

VandAloy 4100 DN

Demin water

Tradebe

11 01 11 / 11 01 98

Effluent System

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Line 2A Medium Phosphorous Nickel plating line, including pretreatments (cleaners and acid etch) as well as

The electroless Nickel plating process and associated rinse tanks.

VandAloy 4100 A

VandAloy 4100 B

VandAloy 4100 DN

Demin water

Hydrochloric Acid (30%)

Nickel Chloride 240g/l

Demin water

Hydrochloric Acid (30%)

Demin water

Effluent System

Alkan

8   (3850l)

Rinse

9   (4000L)

Hydrochloric Acid (30%)

10   (4000L)

Hydrochloric Acid (15%)

11    (4000L)

Nickel Solution

14   (4700L)

Nickel Solution

15   (4700L)

Empty tank

16   (4700L)

Alkaline deruster

130g/l

Nickel Strike

12  (3800L)

Nickel Solution

13  (4700L)

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Tradebe

11 01 11 / 11 01 98 / 11 01 05

Line 4 Medium Phosphorous Nickel plating line, including pretreatments (cleaner and acid etch) as well as

The electroless Nickel plating process.

Uni-Clean 252

1  (393L)

Hydrochloric Acid (15%)

2  (393L)

Nickel Solution

3 (2200L)

Nickel Solution

4 (2200L)

VandAloy 4100 A

VandAloy 4100 B

VandAloy 4100 DN

Demin water

60g/L Uni-Clean 252

Demin water

Hydrochloric Acid (30%)

Tradebe

11 01 11 / 11 01 98

Effluent System

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Filter cake

11 01 09

Tradebe

Filter press

NAOH 32%

Effluent Treatment Process – processing aqueous waste for discharge to sewer

HCL

H2SO4 35%

Ferric Chloride 41.5%

Rinses

NAOH 32%

H2SO4 35%

Drain

v-notch

Macflo 1020

Spent Cleaner

Discharge tank

Clarifier

pH adjustment

tank

Treatment tank

Effluent Treatment Summary

An effluent plant treats our industrial wastewater to ensure it is safe before discharge to the sewage works. Waste liquids from plating—rinse water, spent cleaners, spent acids, and spent electroless nickel—must undergo neutralization and metal removal.

Process Steps

- Transfer ~200 L spent acid, 1000 L spent cleaner, and 6500 L rinse water (volumes may vary) into the treatment tank. Mix for at least 10 minutes to ensure a uniform solution.

- Adjust pH to 3–5 using 35% sulfuric acid or 32% caustic soda.

- Add 40 L ferric chloride and mix for 60 minutes.

- Adjust pH to 7–10, add flocculant as needed, mix 30 seconds, then allow to stand (ideally overnight, minimum 2–4 hours) to compact the filter cake.

- Pump the compacted mixture into a clarifying tank. Treated water overflows into another tank for final pH adjustment if required. The filter cake is pumped to a press for drying.

- Adjusted water pumped into a discharge tank for controlled manual release. All discharged water is automatically sampled and periodically tested by Yorkshire Water.

- Package and dispose of dried filter cake through Innovation Alloys.

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Cumac Optima Brightener

Sulphuric acid 32ml/L

Cumac Optima Make-Up

10ml/L

Copper Plating  Tank – Electrolytic Copper plating

DI Water

Per Ciria C736, Containment Systems for the prevention of pollution, All tanks are contained via physical bund below the tank.  Tanks indicated by a blue X also have an extra layer of containment (extra bund or second skin to tank). Tanks with a red O have direct extraction.

Tradebe

11 02 05

Copper tank 1

Copper sulphate 220g/L

Hydrochloric Acid (36%) 0.2ml/L

Cumac Optima Leveller 0.5ml/L

Copper tank 2