{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Sheet2","Sheet1"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet2","index":0,"n_rows":18,"n_cols":18,"rows_kept":18,"cut":false,"hidden":false,"merged":[]}
[null,"Appendix 38"]
[null,"Capabilities Beyond Engineering - Bund and Operating tanks volume calculations"]
[]
[null,"Bunds must have the volume to contain 110% of the largest single tank on them"]
[null,"Bunds must have the volume to contain 25% of the total volume of tanks on them"]
[null,"Main bund is 100mm deep at its circumference."]
[null,"Site Map showing location of bunds"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Volume Calculations"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"L4 Bund = ","8.16m x 3.26m x 0.2m","= 5.32m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cu Bunds = ","2.52m x 1.5m x 0.43m","=17.32m3"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Main Bund = ","(38.5m x 34.7m x 0.1m)",135.54,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"+ Area under RO tanks","(6.11m x 2.3m x 0.1m)",14.053000000000001,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"- Goods inwards 'triangle'","(6.19m x 6.19m x 0.1m x 0.5)",19.149999999999999,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"- Main Ramp","(4.28m x 4.0m)",17.12,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"- Concrete Plinth","(26m x 1m) ",26,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"- Rear door ramp","(4m x 2m)",8,"m3"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Volume of main bund",null,{"$f":"Q12+Q13-Q14-Q15-Q16-Q17","v":79.322999999999979},"m3"]

{"sheet":"Sheet1","index":1,"n_rows":32,"n_cols":33,"rows_kept":32,"cut":false,"hidden":false,"merged":[[30,26,30,27],[30,3,30,4],[27,1,28,4],[31,1,31,4],[31,24,31,27]]}
[null,"Volumes of tanks in Operation"]
[]
[null,"Volumes in m3",null,"Total Volume:",null,null,null,"Total Volume:",null,null,null,"Total Volume:",null,null,null,"Total Volume:",null,null,null,null,"Total Volume:",null,null,null,null,null,null,null,"Total Volume:",null,null,null,"Total Volume:"]
[null,"Line","Tank",{"$f":"SUM(D5:D27)","v":3.1},null,"Line ","Tank",{"$f":"SUM(H5:H27)","v":12.805000000000003},null,"Line","Tank",{"$f":"SUM(L5:L27)","v":29.7},null,"Line","Tank",{"$f":"SUM(P5:P27)","v":38.450000000000003},null,null,"Line","Tank",{"$f":"SUM(U5:U27)","v":98.5},null,"Line","Tank",{"$f":"SUM(Y5:Y25)","v":12},null,"Line","Tank",{"$f":"SUM(AC5:AC25)","v":5.1859999999999999},null,"Line","Tank",{"$f":"SUM(AG5:AG25)","v":6.5}]
[null,"Stripper",1,0.8,null,"Line 1",1,1.0900000000000001,null,"Line 2",1,4,null,"Line 2A",8,3.85,null,null,"ETP","Equalisation",15,null,"RO Tanks","Feed",2,null,"Line 4",1,2.2000000000000002,null,"Copper","Tank 1",3.25]
[null,null,2,0.8,null,null,2,0.55000000000000004,null,null,2,4,null,null,9,4,null,null,null,"Alkaline",10,null,null,"Store",10,null,null,2,2.2000000000000002,null,null,"Tank 2",3.25]
[null,null,3,1.5,null,null,3,0.55000000000000004,null,null,3,4,null,null,10,4,null,null,null,"Acid",10,null,null,null,null,null,null,"Cleaner",0.39300000000000002]
[null,null,null,null,null,null,4,0.55000000000000004,null,null,4,4.7,null,null,11,4,null,null,null,"Nickel Waste",12,null,null,null,null,null,null,"Acid",0.39300000000000002]
[null,null,null,null,null,null,5,0.55000000000000004,null,null,5,4.7,null,null,12,3.8,null,null,null,"Neutralisation",7.5]
[null,null,null,null,null,null,6,0.55000000000000004,null,null,6,4.7,null,null,13,4.7,null,null,null,"Clarifier",11.5]
[null,null,null,null,null,null,7,0.55000000000000004,null,null,7,3.6,null,null,14,4.7,null,null,null,"Final Neutralisaion",7.5]
[null,null,null,null,null,null,8,0.55000000000000004,null,null,null,null,null,null,15,4.7,null,null,null,"Rinse ",25]
[null,null,null,null,null,null,9,0.55000000000000004,null,null,null,null,null,null,16,4.7]
[null,null,null,null,null,null,10,0.55000000000000004]
[null,null,null,null,null,null,11,0.55000000000000004]
[null,null,null,null,null,null,12,0.55000000000000004]
[null,null,null,null,null,null,13,0.55000000000000004]
[null,null,null,null,null,null,14,0.55000000000000004]
[null,null,null,null,null,null,15,0.55000000000000004]
[null,null,null,null,null,null,16,0.67500000000000004]
[null,null,null,null,null,null,17,0.67500000000000004]
[null,null,null,null,null,null,18,0.67500000000000004]
[null,null,null,null,null,null,19,0.89]
[null,null,null,null,null,null,20,0.55000000000000004]
[null,null,null,null,null,null,21,0.55000000000000004]
[]
[]
[null,"Grand Total Volume stored on main bund:",null,null,null,{"$f":"D4+H4+L4+P4+U4+Y4","v":194.55500000000001},"m3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cu Bunds",{"$f":"1.62*2","v":3.24},"m3"]
[null,null,null,null,null,null,null,null,null,"Theoretical volume to contain Cu Tanks",null,null,null,null,null,null,null,null,"Overflow feed directly onto main bund"]
[null,null,null,null,"Bund Volume:",79.3,"m3",null,null,{"$f":"F30+AF28","v":82.539999999999992},"m3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Bund Volume:",5.32,"m3"]
[null,null,null,"total capacity (volume x 4): ",null,{"$f":"F30*4","v":317.2},"m3",null,null,{"$f":"J30*4","v":330.15999999999997},"m3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"total capacity (volume x 4): ",null,{"$f":"AC30*4","v":21.28},"m3"]
[null,"Single largest possible tank on bund volume",null,null,null,{"$f":"F30/1.1","v":72.090909090909079},"m3",null,null,{"$f":"J30/1.1","v":75.036363636363618},"m3",null,null,null,null,null,null,null,"NB","ETP Working volume = 43 m3",null,null,null,null,"Single largest possible tank on bund volume",null,null,null,114.27272727272727,"m3"]