| Lundwood Secondary Containment Assessment August 2024 |  |
| --- | --- |

Sign-Off Sheet

| Project details |  |
| --- | --- |
| Project number | 331001762 100.2401 |
| Project name | Environmental permitting for IED sites |
| Date | August 2024 |
| Client details |  |
| Client name | Yorkshire Water Service Ltd |
| Client address | Western House Halifax Road Bradford West Yorkshire BD6 2SZ |
| Document details |  |
| Document title | Lundwood Secondary Containment Assessment​ |
| Document version | V002 |
| Report author | Kiran Parmar |
| Report reviewed by | Sam Walmsley |
| Report approved by |  |
| Report by | Stantec Stantec House Kelburn Court Birchwood Warrington WA3 6UT |

Disclaimer This document entitled Lundwood Sludge Treatment Facility (STF) Application for Environmental Permit Variation was prepared by Stantec for the account of Yorkshire Water (the “Client”). Any reliance on this document by any third party is strictly prohibited. The material in it reflects Stantec’s professional judgment considering the scope, schedule and other limitations stated in the document and in the contract between Stantec and the Client. The opinions in the document are based on conditions and information existing at the time the document was published and do not take into account any subsequent changes. In preparing the document, Stantec did not verify information supplied to it by others. Any use which a third party makes of this document is the responsibility of such third party. Such third party agrees that Stantec shall not be responsible for costs or damages of any kind, if any, suffered by it or any other third party as a result of decisions made or actions taken based on this document.

Contents

1	Introduction	4

1.1	Site details	4

1.2	Overview	7

2	ADBA risk assessment tool findings	8

2.1	Class of required secondary containment for Lundwood	8

3	Solution appraisal	10

3.1	Objectives	10

3.2	Sources at Lundwood STF	10

3.2.1	Bulk storage vessels	10

3.2.1.1	Sludge reception, treatment, and handling	11

3.2.1.2	Sludge digestion	14

3.2.1.3	Digested sludge treatment, handling and disposal	16

3.2.2	Tank volumes	18

3.2.3	Engineering and maintenance standards	19

3.3	Existing site surfacing	20

3.4	Pathways	22

3.4.1	Spill modelling	22

3.4.1.1	Modelling limitations and uncertainties	22

3.4.2	Spill scenarios and volumes	22

3.5	PondSIM modelling of unmitigated pathways	24

3.6	Spill pathways	26

3.6.1	Surface drainage	26

3.6.2	Pathway 1	28

3.6.3	Pathway 2	30

3.6.4	Pathway 3	31

3.6.5	Spill pathway summary	34

3.7	Receptors	36

3.8	Source-pathway-receptor summary	37

3.9	Mitigation solutions	38

3.9.1	Surge	43

3.9.2	Jetting	44

3.9.2.1	Multi-tank area 1	45

3.9.2.2	Multi-tank area 2	46

3.9.2.3	Multi-tank area 3	48

3.9.2.4	Digester feed tank	49

3.10	CIRIA C736 compliance and construction.	49

4	Preventative maintenance and inspection regime	50

4.1	Above ground tanks	50

4.2	Below ground level tanks/chambers	50

4.3	Underground pipes	50

4.4	Impermeable surfaces	51

5	Implementation and timescales	52

5.1	Construction	52

6	Conclusions and recommendations	53

7	ARUP Design Overview	54

8	Appendices	55

Appendix 1 - ADBA assessment tool	56

Appendix 2 - CIRIA C736 compliant solution	57

Appendix 3 - Structural integrity note for concrete tanks	59

Appendix 4 - CIRIA C736 jetting calculation	61

Appendix 5 - Example tank inspection report	62

Appendix 6 - (Arup) Secondary Containment Lundwood Maximum Containment Depth Sheet	63

List of Figures

Figure 1. Lundwood STF aerial view, installation boundary in green.   © Google, 2021	5

Figure 2. Process flow diagram Lundwood STF.	6

Figure 3. Flow chart showing the approach taken to provide secondary containment supporting evidence.	7

Figure 4. ADBA risk assessment classification flowchart.	8

Figure 5. ADBA classification matrix.	9

Figure 6. Lundwood sources of risk and site areas.	10

Figure 7. Sludge vessels located in the northern and central section of the site.	11

Figure 8. Sludge vessels located in the eastern section of the site.	11

Figure 9. Sludge import tank.	12

Figure 10. Drum thickener feed tanks (2 no.).	13

Figure 11. Digester feed tank.	14

Figure 12. Digesters (2 no.).	15

Figure 13. Digested sludge storage tanks (2 no.).	16

Figure 14. Liquor return balancing tanks (2 no.).	17

Figure 15. Sludge cake conveyor and pad.	17

Figure 16. Sludge cake storage pad.	18

Figure 17. Lundwood existing site surfaces.	21

Figure 18. Lundwood single tank and multi-tank installation areas.	23

Figure 19. Calculation of digester above ground volumes.	24

Figure 20. Model showing unmitigated result of spills and resulting pathways from existing tanks at Lundwood STF using the CIRIA C736 rule.	25

Figure 21. Lundwood WwTW surface drainage route survey.	27

Figure 22. Pathway 1: pooling potential around the drum thickener tanks.	28

Figure 23 a) elevated bank with rough vegetation, b) curving access road with camber towards kerbed inner section.	29

Figure 24, a) thick vegetation and fenced section near overland flow route, b) fenced section and vegetation along access road.	30

Figure 25. Pathway 2: modelled pooling around the digester area access road and south of site.	31

Figure 26. Potential pooling and pathway around the liquor return balancing tanks and FSTs.	32

Figure 27. Section of dropped kerb on access road near FSTs.	33

Figure 28. Potential flow route for spills passing dropped kerb.	33

Figure 29. Sloping embankment south of the FSTs adjacent to sensitive receptor.	34

Figure 30. Map of numbered receptors at Lundwood. © Google, 2021	36

Figure 31. Mitigation - multi-tank area 1	40

Figure 32. Mitigation - multi-tank area 2	41

Figure 33. Mitigation - multi-tank area 3	42

Figure 34. Mitigation - digester feed tank	43

Figure 35. Surge protection requirements.  Taken from CIRIA C736 pg 54.	43

Figure 36 Jetting potential for multi-tank area 1	45

Figure 37 View from elevated ground to the north of the import tank	46

Figure 38 Jetting potential for multi-tank area 2	46

Figure 39 - Land rises to east of thickener feed tanks	47

Figure 40 Jetting potential for multi-tank area 3	48

Figure 41 Jetting potential for digester feed tank	49

Appendix Figure 1. ADBA spreadsheet screenshot	56

Appendix Figure 2. CIRIA C736 jetting calculation to determine jetting solution.	61

Appendix Figure 3. Example equipment inspection report	62

List of Tables

Table 1. Lundwood STF tanks, capacities, age, and construction materials.	19

Table 2. Volume of material used in spill modelling scenarios.	23

Table 3. Surface pathways from the key assets at Lundwood.	35

Table 4. Receptor number and description.	36

Table 5. Source-pathway-receptor summary	37

Table 6. Containment volume calculations.	39

Table 7. Secondary containment implementation stages and schedule.	52

Appendix Table 1.  Lundwood bunding solution design specification and dimensions.	57

# Introduction

As part of the Industrial Emissions Directive (IED) permit application for Lundwood Sludge Treatment Facility (STF), Yorkshire Water (YW) has undertaken an assessment of the significance and potential environmental risks associated with a loss of containment of process vessels. YW has also reviewed existing provisions and potential improvement options against Best Available Techniques (BAT) principles, in alignment with CIRIA C736.

Lundwood STF falls under the IED as a Part A(1) installation  by virtue of exceeding the 100t/d capacity limit for anaerobic digestion (AD. The permit will cover raw sludge storage, handling and thickening, digested sludge storage, handling and dewatering, sludge cake secondary treatment and storage, biogas storage, utilisation and flaring. This document focuses on the secondary containment aspects of the permit requirements, in particular the application of BAT, and should be viewed in parallel with the main permit application document, in particular Section II: Technical Description, Section III: Accident Risk Assessment and Appendix 4: Site Condition Report.

## Site details

Lundwood Wastewater Treatment Works (WwTW) was constructed circa 1960 in the village of Lundwood, 3.2km east of Barnsley, South Yorkshire.  Lundwood STF is located adjacent to the WwTW.  The River Dearne is located to the south and the STF installation is bordered primarily by farmland to the south and east and by housing to the North and to the Northwest. Lundwood STF treats indigenous sludge from the co-located WwTW and liquid sludge imported from other YW WwTW.

An aerial view of Lundwood STF along with its installation boundary is shown Figure 1. The key activities at Lundwood STF are illustrated via a process flow diagram in Figure 2. Key activities include sludge thickening; anaerobic digestion; biogas handling and combustion; sludge dewatering and associated routes of gaseous, liquid, and solid materials and energy vectors. These processes are further discussed in Section 3.2.1.

Figure 1. Lundwood STF aerial view, installation boundary in green.   © Google, 2021

Figure 2. Process flow diagram Lundwood STF.

## Overview

YW commissioned Stantec to assess existing provisions and, where necessary, improvement options for secondary containment at the site. Stantec have provided risk-based supporting evidence to accompany the permit application, which demonstrates the most appropriate solution(s) for BAT compliance using CIRIA C736 standards. To fully understand the requirement for secondary containment and to provide environmental protection at Lundwood, two different industry standard tools have been used, these are shown within the flow chart in Figure 3.

Firstly, the Anaerobic Digestion and Biogas Association (ADBA) secondary containment risk assessment tool has been applied to assets at Lundwood. The ADBA assessment tool uses a risk-based methodology to determine the class of secondary containment systems required at a site, based on an assessment of sources, pathways and receptors, and the control measures which already provide protection.

As an existing installation in continuous operation, retrospectively applying a standard secondary containment bund to all sludge tanks and containers may present significant technical, operational, safety and logistical challenges. It is also noted that the location of Lundwood STF within a wider wastewater treatment works (WwTW) presents opportunities in terms of utilising existing YW assets as part of the pollution containment and prevention solution.  Recognising this limitation, a bespoke source, pathway, receptor approach has been developed by Stantec and applied to identify and risk assess bunding solutions in line with the ADBA approach.  These findings have then been used to develop as well site-specific options for secondary containment.

Figure 3. Flow chart showing the approach taken to provide secondary containment supporting evidence.

# ADBA risk assessment tool findings

The ADBA Risk Assessment Tool is based on CIRIA C736 requirements for the prevention of pollution: including secondary and tertiary containment, and other measures for industrial and commercial premises. An assessment is presented in Appendix 1 and the findings are summarised in this chapter.

## Class of required secondary containment for Lundwood

To identify the class of containment deemed to provide sufficient environmental protection in the ADBA Risk Assessment, the tool uses a source, pathway, receptor model. This identifies hazards posed to the environment and assigns a class of containment based on the site hazard rating and likelihood of loss of primary containment. The approach is summarised in Figure 4 below.

Figure 4. ADBA risk assessment classification flowchart.

The ADBA Risk Assessment Tool scored the source element as ‘High risk’, pathway elements as ‘High risk’ and the receptor element as ‘High risk’ at Lundwood owing to the significant volumes of sewage sludge stored on site and site drainage pathways to the sensitive receptor, the River Dearne. In summary, this assessment approach indicates that Lundwood STF has an overall site hazard rating of ‘High Risk’. The likelihood of failure was ‘Low Risk’ due to the type of infrastructure involved and the mitigations at the site e.g., regular tank inspections and level sensors.

According to Table 4 within the ADBA tool (box 2.2 CIRIA C736), reproduced in Figure 5 below, the combination of a high site hazard rating and a low likelihood rating, gives the overall site risk as medium. The indicated class of secondary containment for Lundwood STF was therefore deemed as being Class 2.

Figure 5. ADBA classification matrix.

The ‘Lundwood STF ADBA Secondary Containment Risk Assessment’ outlines the information and data utilised in greater detail, as well as the assumptions applied to undertake a secondary containment risk assessment. The requirement for ‘Class 2’ type secondary containment within Lundwood STF will be used to inform the next stage of secondary containment assessment, carried out by Stantec to support the permit application process (See Chapter 3).

# Solution appraisal

## Objectives

The purpose of this stage of the assessment is to determine the significance and potential environmental risks associated with a loss of containment from sludge vessels within the Lundwood STF, and to review existing provisions and potential improvement options against BAT principles, including CIRIA C736. As described previously, this stage of the process is informed by the outputs of the ADBA tool, but also considers options which are outside the scope of the ADBA scoring system utilising a bespoke methodology which adopts source-pathway-receptor principles in a qualitative risk-based framework.

## Sources at Lundwood STF

The sources of risk which have been identified at Lundwood as shown in Figure 6. These STF operational assets comprise of sludge import, thickening, digestion, dewatering and cake storage areas.

Figure 6. Lundwood sources of risk and site areas.

### Bulk storage vessels

The bulk storage vessel locations are shown and labelled in Figure 7 and Figure 8. Further description of how these vessels are utilised, the sources of risk, existing controls and mitigations associated with the STF is provided in the discussion.

Figure 7. Sludge vessels located in the northern and central section of the site.

Figure 8. Sludge vessels located in the eastern section of the site.

#### Sludge reception, treatment, and handling

Lundwood STF treats the following sewage sludges:

Indigenous primary sludges and surplus activated sludge (SAS) arising from sewage treatment processes operating within the wider Lundwood WwTW that are piped directly to the STF.

Liquid sludges generated by other YW Wastewater Treatment Works (WwTW) (with lower capacity or capability for treating sludges on-site) that are imported to Lundwood STF for additional treatment.

Imported liquid sludge is delivered to site by tanker. The tanker unloads at the dedicated sludge import area and sludge is pumped (using vehicle mounted pumps) into the sludge screen feed tank (Figure 9, 150 m3 covered steel tank). The maximum load is typically 28 tonnes with unloading taking up to 30 minutes. Only appropriately authorised vehicles can discharge at the site. This is controlled using a ‘WaSP’ logger; valves on the discharge pipework will only open when a driver presents appropriate authentication to the system. The WaSP logger records the source of the sludge, the time and date of delivery, the total volume discharged and average percentage dry solids of the load.

Figure 9. Sludge import tank.

After screening, imported liquid sludge is pumped via a sub-surface concrete sump, in pipework (largely underground) to the thickener feed tanks (Figure 10, 2 no. 1,589 m3 covered steel tanks). These tanks are air mixed and operate in fill / draw mode with tanks changing over every 24 hours. The tanks are covered with headspace air extracted and routed to a two-stage odour control unit.

Indigenous SAS and primary sludge from the wider Lundwood WwTW is piped directly to the thickener feed tanks and mixed with the imported screened liquid sludge prior to onward transfer to the drum thickener building.

Figure 10. Drum thickener feed tanks (2 no.).

Sludge from the thickener feed tanks is then transferred to the thickener building via above and below ground pipework serving two thickening process streams, which operate on a duty/standby basis.  Each sludge stream comprises a dedicated thickener feed pump drawing blended sludge, a polymer dosing pump drawing made-up polymer, a flocculation tank and a pair of drum thickeners (thus there are four thickeners in total). Concentrated liquid polymer is diluted with potable water, then mixed with treated final effluent as a carrier and mixed with the sludge in the flocculation tank.  Each flocculation tank feeds two drum thickeners at an equal rate.  The polymer encourages separation of water and sludge as the sludge is rotated in the drum to remove excess liquid. The resulting liquor is transferred to a wet well located to the west of the thickener feed tanks and from there is pumped back to the WwTW for full treatment.  Each sludge stream has been sized with sufficient capacity to process site daily throughput requirements over a 16-hour period i.e., there is adequate redundant capacity in the event of plant failure.

The drum thickeners are equipped with automatic spray bars which provide continual self-cleaning. In addition, an automatic hot wash system is run periodically in accordance with the planned maintenance regime.  The hot wash is designed to break down any fats that would blind the drum filter material.  The automatic spray bars operate using treated final effluent and the hot wash system utilises mains potable water.

The liquid polymer delivery point is located in the roadway outside the thickener building; liquid polymer is delivered in 1m3 IBCs and pumped from these to a 10 m3 bulk storage tank located within the thickener building.  Located above the same concrete sump bund within the thickener building as the bulk storage tank is the 5 m3 capacity polymer solution storage tank containing the diluted polymer solution.

Best available techniques for sludge reception, treatment and handling includes trace heating, reducing fracture on freezing and largely automated PLC. PLC includes level sensors to reduce risk of tank overtopping, resulting in contamination and potential odour generation. Tanks also have an emergency overspill facility connected to site drainage (that is discharged back to the WwTW inlet) as a last line of defence to prevent overtopping.

#### Sludge digestion

The thickened sludge is transferred to a 712 m3 digester feed tank (Figure 11). This tank is of concrete construction, mixed and covered. Sludge is passed forward continually from this tank to the anaerobic digesters (Figure 12, 2 no. 2,056 m3 concrete tanks). The digesters are located on steeply sloping ground and therefore are partly buried below ground on one side, with approximately an above ground volume of 441 m3. The anaerobic digesters operate as a continuous process with sludge being added and treated sludge extracted. The two digesters have a typical feed rate of around 120 m3/day combined; the combined maximum feed rate is 308m3/day (at 6% dry solids) giving a 12-day retention time as required by Hazard Analysis and Critical Control Points (HACCP) controls.  The digesters are mixed by gas mixing systems, which utilise biogas from the headspace of each digester; the gas is compressed and then reintroduced using an array of mixing nozzles on the floor of the digester.

Figure 11. Digester feed tank.

A hot water circuit provides heating to ensure optimum conditions for digester microbial activity.  Potable water is heated to around 70°C by the CHP and/or boiler.  This hot water then heats the digester using tube-in-tube, counter-current heat exchangers. Sludge from the digesters is continually recirculated around the heat exchangers using 2 no. (duty/standby) recirculation pumps per digester.  A 3-way modulating valve on the water side moderates the amount of hot water that passes into the heat exchanger, depending on the heat demand of the digesters.

Grit build up within digesters is a normal feature of operation; the digesters are cleaned out (including accumulated grit) every 10 years as part of the planned periodic inspection which also includes an internal and external inspection of tank integrity and replacement of instrumentation and gas mixing equipment as required.

An automatic anti-foam dosing system is in place to control digester foaming.  This system uses a radar level probe in the digester headspace and compares this to the pressure level sensor at the bottom of the digester to determine the depth of foam. Upon detection of foam, treated final effluent is sprayed into the digester head space through nozzles in the digester roof.  If this is not effective in breaking up the foam, a chemical anti-foam is mixed with treated final effluent and dosed into the headspace of the digester via the same spray nozzles.  This system includes operator-adjustable dosing setpoints and failsafe systems; if the foam level continues to increase mixing systems are inhibited and if this continues the digester feed will be inhibited.  Antifoam is stored in 20 litre plastic containers on a drip tray located within the digester compound prior to transfer to the integrally bunded antifoam dosing tank (approximate capacity of 0.5m3).

Figure 12. Digesters (2 no.).

A boiler is available for use as an alternative heat source for the digesters.  The boiler can be fired by either biogas or fuel oil and has a thermal input of approximately 833 kW. This is located within the same building as the CHP (in an adjacent room) and combustion products are discharged via a 3.5m high (approximately) stack located to the rear of the building. In normal operations boiler use is limited as heat recovery from the CHP engine meets the digester heat demand. Fuel oil used as back up supply for the boilers is stored within a 35,000 litre integrally bunded steel tank.

Best available techniques for sludge digestion include largely automated PLC, monitoring for optimum digester health and foam levels to avoid potential loss of containment, including an anti-foaming system. Additionally, an inspection and testing programme for above and below ground vessels, pipes and valves is in place.  This incorporates a combination of visual examinations and non-destructive testing (e.g., ultrasonic thickness measurements).

#### Digested sludge treatment, handling and disposal

Digested sludge is gravity fed from the digesters to the adjacent digested sludge balance tanks (Figure 13, 2 no. concrete open topped tank with capacity of 880m3). These tanks are periodically mixed to prevent settlement and anoxic conditions.  Powdered polymer stored in 750kg bags is dispensed via a hopper dosing system which feeds a polymer ‘ageing’ tank where the powdered polymer is mixed with potable water and transferred to a stock tank (approximate capacities of 6m3).  The polymer solution is injected into the sludge stream and taken to the digested sludge dewatering centrifuge where the sludge coagulates and supernatant liquor is removed by centrifugal forces

Figure 13. Digested sludge storage tanks (2 no.).

Dewatered liquor is transferred to two liquor balancing tanks (Figure 14, covered steel tanks, each with a capacity of 250 m3) prior to transfer to the WwTW for full treatment.

The final digested and dewatered sludge cake is transferred via a conveyer from the centrifuge up over a push-wall and onto the cake pad (Figure 15). The area under the conveyer and adjacent sludge cake pads are an engineered impermeable surface, with water runoff collected in drains running along the bottom edge of the pad. These liquids are pumped back to the WwTW for full treatment.

Figure 14. Liquor return balancing tanks (2 no.).

Figure 15. Sludge cake conveyor and pad.

Once on the cake pad, sludge cake is moved by mechanical loaders into storage rows (Figure 16). There is no lime addition at Lundwood STF; instead, cake is stored in piles according to age and is left to mature for a minimum of six weeks in accordance with HACCP requirements. Approximately 3,000 tonnes sludge cake will normally be held on site at any one time.  However, the maximum storage capacity of the cake pad is significantly greater than this, up to 12,750 tonnes; greater volumes may be stored on site in emergency/abnormal conditions such as following processing problems at other YW sites or in extreme weather conditions when landspreading operations are temporarily paused.  Once maturation is complete, sludge cake is removed from site and landspread in accordance with legislative requirements.  Samples of digested, matured cake are taken every 3 months, or whenever a Critical Control Point (CCP) (e.g., digestion retention time or temperature) is not within specification and analysed for metals and pathogens to ensure HACCP standards are being met.

Figure 16. Sludge cake storage pad.

The best available techniques for digested sludge treatment, handling and disposal comprises of an engineered cake pad with leachate and washwater collection for treatment at the WwTW, and an inspection and testing programme for pipes and valves, which include surveys using in-pipe leak detection technology.

### Tank volumes

The storage volumes, date constructed and construction materials of the sludge and non-sludge tanks within the STF are summarised in Table 1.

Table 1. Lundwood STF tanks, capacities, age, and construction materials.

| Tank | Size m3 (each tank) | Year constructed | Construction material |
| --- | --- | --- | --- |
| 1 no. sludge import tank | 150 | 2009 | Steel |
| 2 no. drum thickener feed tanks | 1,589 | 2019 | Steel |
| 2 no. liquid polyelectrolyte tank (neat and mixed) | 10 5 | 2019 | PE |
| 1 no. digester feed tank | 712 | 2008 | Concrete |
| 2 no. digesters | 2,056 (a441) | 1962 | Concrete |
| 2 no. digested sludge storage tanks | 880 | 1970, 1971 | Concrete |
| 2 no. polymer tanks (stock and ageing) | 6 | 2009 | Steel |
| 1 no. potable water tank | 60 | 2002 | PE |
| 2 no. liquor return balancing tanks | 250 | 2002, 2015 | Steel |
| 1 no. gas oil tank | 35 | 2011 | Steel |

a volume of sludge stored above ground for subsurface installations.

### Engineering and maintenance standards

YW technical standards define the types of assets that meet the requirements of the business, including how they should be built and then maintained. In relation to Lundwood, this covers:

Design and construction of all assets, including selection of appropriately qualified design and build contractors.

Procedures for inspection and testing of storage vessels, including internal and external inspections, thickness assessment and non-destructive testing.

Regular inspections of above ground assets and associated pipework at defined intervals.

Documented log of any actions arising because of these inspections.

YW’s asset standards have been developed over many years and where relevant comply with Civil Engineering Specification for the Water Industry (CESWI) Seventh Edition March 2011 and the Water Industry Mechanical and Electrical Specifications (WIMES 9.02).

Contractors involved in the design/build of the Lundwood scheme were YW framework contractors, appointed following a rigorous EU tender process; this process involved an assessment of experience, technical competency, design capability and quality procedures.

The combination of all these measures significantly reduces the risk of a catastrophic tank failure, thus reducing the likelihood of secondary containment being required.  Nonetheless, it is recognised that the risk of a catastrophic tank failure cannot be eliminated, and external factors could always arise leading to very low likelihood, high consequence events (such as missile generation arising from other plant failure, domino effects or force majeure, for example an aircraft impact or terrorist attack).

## Existing site surfacing

Most of the active process areas within the installation are covered by buildings and hardstanding, with some peripheral areas of soft landscaping (grass and gravel cover). Surfacing was generally observed to be in good condition across the site with no significant evidence of cracks or erosion. Site surfacing for Lundwood is illustrated in Figure 17.

Hardstanding

Grass

Buildings

Tanks

Other assets

Gravel

Figure 17. Lundwood existing site surfaces.

## Pathways

Pathways are the routes by which pollutants could travel from a source to the point where they could cause damage, the receptor. The potential pathways in this assessment were determined using computation flow modelling based on defined source spillage volumes. The modelling approach, limitations and spill volumes are outlined in the following sections, allowing the principal pathways to be identified.

### Spill modelling

To model the potential impact of spills to the environment from the various sludge treatment assets at Lundwood STF and defined credible pathways, YW has used PondSIM, a computational overland flow modelling tool. PondSIM can represent the flow of a liquid spill across an area of ground, taking account of local topography and flow restrictions (such as barriers). Applying this to the Lundwood site has allowed visualisation of the likely effects of a spill occurring within each of the key areas of the permitted installation.

#### Modelling limitations and uncertainties

As with any computational modelling tool, there are several assumptions required and associated modelling limitations and uncertainties:

- PondSIM is designed to model the overland flow of water; as such it is not able to account for the typically higher viscosities associated with sludge, which results in a larger modelled inundation extent than would be expected.

- The model cannot allow for flow to drains and other subsurface features.

- Surge is not accounted for within the model. Instead, this will be allowed for by ensuring final designs consider CIRIA C736 recommendations, while recognising the loss of kinetic energy as viscous sludge travels over flat ground.

- The model assumes that no mitigation measures are put in place following an incident to curtail flow.

- The model assumes that the full modelled volume spills from a single point.

- Assets are treated as simple flow barriers in the model, which may result in deflections being observed where flow would spread out.

Therefore, the modelled outputs are a worst-case inundation scenario resulting from sludge spills at Lundwood. Notwithstanding these limitations, the use of PondSIM is considered appropriate as an initial screening tool for this study.

### Spill scenarios and volumes

YW has followed CIRIA C736 guidance on spill volumes to be modelled i.e., values equivalent to the containment provided by bunded tanks have been used. For a single tank the volume should be calculated based on 110 per cent of the capacity of that tank. For multi-tank installations, the containment volume should be calculated based on 25 per cent of the total capacity of all the tanks in a common area (which assumes that it is unlikely that more than 25 per cent of tanks will fail simultaneously), or 110 per cent of the largest tank, whichever is greatest. Tanks which are hydraulically linked should be treated as if they were a single tank.

The Lundwood sludge storage tanks and treatment processes are installed as either multi-tank or single tank installations, as shown in Figure 18, where blue is a single tank installation and numbered yellow areas are multi-tank installation areas. Non-sludge vessels (i.e., polymer, water, and gas oil tanks etc.) have not been included within the PondSIM modelling. This is due to the site already having appropriate secondary containment measures in place, in accordance with YW’s asset standards. The CIRIA C736 rule spill modelling scenario and associated containment volumes is listed in Table 2. As the digesters at Lundwood are located partially below ground, the below ground volume can be considered contained. Therefore, the above ground volume, as shown in Figure 19, was used in the calculation of modelling volumes.

Table 2. Volume of material used in spill modelling scenarios.

| Scenario | Capacity calculation | Modelled containment volume (m3) | Modelling reference |
| --- | --- | --- | --- |
| CIRIA C736 rule | Single tank and multi-tank installations | 3,774 | Figure 20 |

Figure 18. Lundwood single tank and multi-tank installation areas.

Figure 19. Calculation of digester above ground volumes.

  - PondSIM modelling of unmitigated pathways

This section presents the modelling outputs showing unmitigated spills and resulting pathways from the identified sources, via surface pathways as calculated by PondSIM to the identified receptors.

This modelling assessment considered the effect of a simultaneous loss of containment from all the single and multi-sludge tank areas at the STF. Therefore, the model presented in Figure 20 represents the CIRIA C736 scenario, recognising limitations discussed in 3.4.1 Spill modelling. The location and direction of the modelled spills and adjacent treatment assets are discussed in section 3.6 Spill pathways.

It is important to note that owing to the limitations described in 3.4.1.1, and the specific topography of the Lundwood site, it is not felt that PondSIM outputs at Lundwood are representative of the likely impact of a tank collapse. The detail of this is discussed in following sections, but common themes are:

- PondSIM models fluids as having very low viscosity. In the hilly areas of a site such as Lundwood, this leads to fluids travelling significant distances. In practice, pooling is likely to occur i.e., large spread in a small area, rather than long ‘streams’ covering significant distances.

- The aerial survey used to support the modelling is imperfect. At Lundwood there are several small surface features which would be likely to retain sludge, that were not captured in the aerial survey.  See photos in the following section for additional detail.

- PondSIM cannot model capture of liquid within site drainage system. In practice, the modelled flows travel over some areas of ground that has contained drainage which will capture a proportion of spilt material.

Figure 20. Model showing unmitigated result of spills and resulting pathways from existing tanks at Lundwood STF using the CIRIA C736 rule.

## Spill pathways

### Surface drainage

A surface water drainage survey was completed at Lundwood WwTW in October 2020. The survey mapped the location of gullies and manholes, separating them into contained and non-contained drainage routes, as illustrated in Figure 21. Surface water drainage routes shown in red are routed to the inlet of the WwTW i.e., contained. Lundwood STF has not been found to have surface water drainage that discharges directly to River Dearne, although there are roof water downpipes that discharge to soakaway (i.e., are non-contained).  The downpipes would not be affected by a sludge spill and are not considered further within this report.

Two areas of uncertainty have been identified in respect of the drainage system in two specific areas within the installation.  These are as follows:

- Effluent and surface water runoff from the CHP/boiler compound and roadway are directed to a drain which is reported to have collapsed.  This source comprises surface water runoff, and potentially condensate from the biogas pipeline feeding the boilers/CHP and boiler blowdown.  YW is committed to investigating, and as required repairing the drains (prior to issue of the permit) in this area so that all liquors arising are returned to the WwTW for full treatment.

- Surface water runoff from the digester area is directed to a drainage route which cannot be fully traced due to line length.  Adopting a precautionary approach, as this line may also include condensate from the biogas pipeline feeding the flare, YW is committed to investigating the drains (prior to issue of the permit) to ensure that all liquors arising are returned to the WwTW for full treatment.

In summary, the unmitigated spill modelling demonstrates that a sludge spill does not have potential to reach a receptor via site drainage.  Addition of bunding will further contain spills.  No amendments to existing site drainage are required.

Figure 21. Lundwood WwTW surface drainage route survey.

### Pathway 1

The unmitigated modelled spills show potential pooling of sludge on permeable grassy surfaces predominantly around the drum thickener feed tanks and a direct route (Pathway 1) to a sensitive receptor, stemming from the multi-installation area 2 and the single digester feed tank, as shown in Figure 22. This area, as part of the wider field, was previously occupied by settlement tanks, which have been decommissioned and filled in to create a site for future development. Therefore, the surface is likely to be permeable. Contained surface water drainage is present within the drum thickener feed tank compound, this returns to the WwTW for treatment.

There is low confidence in the modelled route of sludge shown in Pathway 1 due to the limitations of PondSIM modelling, and its inability to reflect surface drainage containment, spill viscosity and rough terrain. The model shows the spill continuing along the access road, over thick vegetation and into a ditch which allows inundation of a north-south flowing overland flow route, which is hydraulically connected to the west-east flowing drainage ditch which confluences with the River Dearne. Whilst the model at this section of site is unlikely to be representative of a true sludge spill, this spill pathway shows a route to the sensitive receptor, River Dearne.

Figure 22. Pathway 1: pooling potential around the drum thickener tanks.

NB. This output is heavily affected by the limitations of PondSIM.

In support of this assessment, photographic evidence Figure 23a) shows a potential sludge spill would have to navigate over a slight incline covered in rough vegetation before reaching the ditch, additionally Figure 23b) shows that the access road has a camber towards the inner kerbed section. Given the rheology (i.e., the flow and deformation) of sludge, it is likely that a sludge spill would tend to spread in the area near the source (thickener feed tanks), with only small amounts travelling along the road toward the boundary fence.

Figure 23 a) elevated bank with rough vegetation, b) curving access road with camber towards kerbed inner section.

Furthermore, Figure 24a) shows thick vegetation between the overland flow route and palisade fencing, whilst Figure 24b) shows vegetation butted up against the lower section of fence. Given the distance from the source it is unlikely that significant quantities of sludge material would penetrate this section to reach the overland flow route, as an operational clean up team would be deployed within 24 hours, further mitigating impact to the sensitive watercourse.

In summary, Pathway 1 was generally given a low confidence rating due to:

- Surface drainage located in the drum thickener compounds

- Sludge rheology i.e., properties of a thick viscous material.

- Camber present to the inner section of the road away from the overland flow route.

- Thick and rough vegetation present prior to the ditch and in between the access road and overland flow route.

Figure 24, a) thick vegetation and fenced section near overland flow route, b) fenced section and vegetation along access road.

### Pathway 2

Figure 25 shows sludge spills from the multi-tank installation area 3, i.e., the digester compound, and a route to a sensitive receptor (Pathway 2). Modelling results show that the sludge pools within the hardstanding surface areas in the digester compound and access roads, before flowing down to the south of the site along another access road and adjacent to the ASPs. The sludge spill continues downhill, flows between kiosk buildings, through thick vegetation before reaching the drainage ditch that confluences with the River Dearne. The spill pathway represented here shows a direct pathway to the sensitive receptor.

Pathway 2 is also given a low confidence due to the limitation of the PondSIM modelling software. Whilst a high degree of confidence is given for the sludge flow from the digester compound to the access roads due to the elevation and volumes contained, it is very unlikely a spill would travel down to the site of the site due to the distances involved. In practice a sludge spill would spread rather than forming a long stream. The large surface area of the access roads has potential to contain a significant volume of sludge preventing onward flow toward the watercourse.

In summary, Pathway 2 was generally given a low confidence rating due to:

- Sludge rheology i.e., properties of a thick viscous material resulting in a tendency to form large pools, rather than the long streams created in PondSIM.

- Distances involved from multi-tank installation 3 to the sensitive receptor.

- Thick vegetation present at the south of the site.

- Surface drainage features present along the access roads.

Figure 25. Pathway 2: modelled pooling around the digester area access road and south of site.

NB. This output is heavily affected by the limitations of PondSIM.

### Pathway 3

Pathway 3, a direct / indirect pathway to a sensitive receptor is illustrated in Figure 26. A medium confidence rating is given to Pathway 3 due to the close vicinity of the multi-tank installation area 1 to the drainage ditch that confluences with the River Dearne.

The model shows the spill starting at the tanks, crossing the access road between the tank installation area and FSTs and flowing through a dropped kerbed area, as shown in Figure 27. A high confidence rating for Pathway 3 cannot be given due to the likely significant effect of small elevation changes in this area e.g., the height of the dropped kerb and thick vegetation. In reality, a sludge spill is unlikely to impact the FSTs due to loss of velocity at the kerb adjacent to the road, and the lip around the tanks, also shown in Figure 26. Any sludge entering the FST area would flow and pool around the FSTs and given the relatively low viscosity of liquor return balancing tanks content. The model shows the spill continuing south from the FST heading downhill, through palisade fencing and thick vegetation before entering the drainage ditch.

Figure 28 shows an alternative, and perhaps more likely, flow route for spills in this area.  The fall on the road is towards a site building near the boundary fence.  In front of this building is a surface water drain, any liquid entering this is contained and ultimately returned for treatment within the WwTW.  This has potential to prevent spills from the liquor return tanks spreading to permeable surfaces.

A medium confidence rating was given to this pathway, a conclusion supported by photographic evidence provided in Figure 29, which shows a sloping route to the receptor.

In summary, Pathway 3 was given a low confidence rating due to the:

- Likely impact of minor gradient and elevation changes in this area, which have not been accurately captured in aerial survey data.

- Potential for liquor flow to be captured within existing site drainage.

- Thick and rough vegetation present between the palisade fence and sensitive receptor.

- Mixed sludge rheology i.e., moderate, and low viscosity material from sludge import and liquor tanks respectively.

Considering the evidence for the requirement for enhanced environmental protection, mitigative options will be considered for Pathway 3, but additional investigation is required to collect data to support the decision-making process.

Figure 26. Potential pooling and pathway around the liquor return balancing tanks and FSTs.

NB. This output is heavily affected by the limitations of PondSIM and is unlikely to be as severe in the event of a real-world spill.

Figure 27. Section of dropped kerb on access road near FSTs.

Figure 28. Potential flow route for spills passing dropped kerb.

Figure 29. Sloping embankment south of the FSTs adjacent to sensitive receptor.

### Spill pathway summary

The table below lists the pathways associated with tank failure at Lundwood determined using the PondSIM model.  Full model results are presented in Section 3.4.

Table 3. Surface pathways from the key assets at Lundwood.

| Common Area / Tank | Surface Pathways | Comments |
| --- | --- | --- |
| Multi-tank installation area 1. (Sludge import tank, 2 no. liquor return balancing tanks) | Pathway 3 – overall low confidence. Overland run-off over mostly sealed surfaces to: - South of the site towards the FSTs | Spill volume captured on existing site access roads hardstanding areas before reaching a permeable grassy section and a sensitive receptor south of site. Local surface water drainage in this area is contained and is returned to the WwTW for treatment prior to discharge. |
| Digester feed tank | Pathway 1 – overall low confidence. Overland run-off over mostly sealed surfaces to: - The drum thickener feed tank and OCU compound. - West of the site towards the drainage ditch. | Spill flows across and is captured on hardstanding and road surfaces before reaching a drainage ditch at the western section of the whole site. Surface water drainage is present in the digester feed and drum thickener feed tank compound areas, this is contained and returned to the main WwTW for treatment prior to discharge. |
| Multi-tank installation area 2. (2 no. drum thickener tanks) | Pathway 1 – overall low confidence. Overland run-off over mostly sealed surfaces to: - The drum thickener feed tank and OCU compound. - West of the site towards the drainage ditch. | Spill flows across and is captured on hardstanding and road surfaces before reaching a drainage ditch at the western section of the whole site. Surface water drainage is present in the digester feed and drum thickener feed tank compound areas, this is contained and returned to the main WwTW for treatment prior to discharge. |
| Multi-tank installation area 3. (2 no. digesters, digesters, 2 no. digested sludge storage tanks) | Pathway 2 – overall low confidence. Overland run-off over un-sealed surfaces to: - Northern access road. - Central access road and ASP area. - Sensitive receptor south of the site. | Principal spill volume captured on existing site hardstanding areas within access roads, before reaching a before reaching a permeable grassy section and sensitive receptor south of site. Surface water drainage in this area is contained and returned to the main WwTW for treatment prior to discharge. |

## Receptors

To complete the source pathway receptor model, a review of sensitive receptors was conducted in conjunction with the accompanying ADBA Assessment and Site Condition Report (Appendix 4) detailing site setting, geology and groundwater. These were identified based on professional judgement, modelling results and potential flow paths which may take any cardinal direction in lower lying areas. Figure 30 shows the receptors identified which could theoretically be impacted by a loss of containment from sludge vessels at Lundwood.

Table 4 lists the type of pathway potentially leading to each receptor e.g., indirect, such as via FSTs, permeable surfaces or direct to the environment, e.g., a flow path into the River Dearne.

Figure 30. Map of numbered receptors at Lundwood. © Google, 2021

Table 4. Receptor number and description.

| Receptor no. | Receptor |
| --- | --- |
| 1 | Drainage ditch merging with the River Dearne (including adjacent habitats). |
| 2 | Ground / groundwater – areas around and within the cake pads. |
| 3 | Ground / groundwater - area around sludge import and liquor balancing tanks, including the FSTs. |
| 4 | Ground / groundwater - areas surrounding the westerly FSTs. |
| 5 | Ground / groundwater - areas surrounding drum thickener, digester feed tanks and ASPs. |
| 6 | Ground / groundwater - areas including and surrounding the digester compound (digester and digested sludge tanks). |
| 7 | Ground /groundwater – area surrounding tanks. |
| 8 | Overland flow route – level linked to rainfall |

## Source-pathway-receptor summary

A summary of the receptors at risk following the modelling of spill pathways from identified sources at Lundwood STF is listed in Table 5.

Table 5. Source-pathway-receptor summary

| Common Area / Tanks | Surface Pathways | Receptors at risk |
| --- | --- | --- |
| Multi-tank installation area 1. (Sludge import tank, 2 no. liquor return balancing tanks) | Pathway 3 – overall low confidence. Overland run-off over mostly sealed surfaces to: - South of the site towards the FSTs. | - Receptor 3 - Ground / groundwater - area around sludge import and liquor return balancing tanks, including the FSTs [medium confidence]. - Receptor 1 – Drainage ditch merging with the River Dearne (including adjacent habitats) [low confidence]. |
| Digester feed tank | Pathway 1 – overall low confidence. Overland run-off over mostly sealed surfaces to: - The drum thickener feed tank and OCU compound. - West of the whole site towards the drainage ditch. | - Receptor 5 - Ground / groundwater - areas surrounding drum thickener, digester feed tanks and ASPs [medium confidence]. - Receptor 7 - Ground /groundwater – area surrounding tanks [low confidence]. - Receptor 8 - Overland flow route – [low confidence]. |
| Multi-tank installation area 2. (2 no. drum thickener tanks) | Pathway 1 – overall low confidence. Overland run-off over mostly sealed surfaces to: - The drum thickener feed tank and OCU compound. - West of the site towards the drainage ditch. | - Receptor 5 - Ground / groundwater - areas surrounding drum thickener, digester feed tanks and ASPs [medium confidence]. - Receptor 7 - Ground /groundwater – area surrounding tanks [low confidence]. - Receptor 8 - Overland flow route – [low confidence]. |
| Multi-tank installation area 3. (2 no. digesters, digesters, 2 no. digester sludge storage tanks) | Pathway 2 – overall low confidence. Overland run-off over un-sealed surfaces to: - Northern cake pad. - Southern Lagoons. - Surface water drain south of the site. | - Receptor 6 - Ground / groundwater - areas including and surrounding the digester compound (digester and digested sludge tanks) [high confidence]. - Receptor 2 - Ground / groundwater – areas around and within the cake pads [medium confidence]. - Receptor 3 - Ground / groundwater - area around sludge import and liquor return balancing tanks, including the FSTs [low confidence]. - Receptor 1 - Drainage ditch merging with the River Dearne (including adjacent habitats) [low confidence]. |

## Mitigation solutions

An iterative process was completed to develop bunding options that provide environmental protection in accordance with CIRIA C736, including different methods for achieving impermeable surfaces within the bunded area. Determination of the preferred solution considered financial viability, sustainability to reduce impacts from embodied carbon and availability of materials to allow timely implementation given the timeframes of meeting compliance.

The solution identified is illustrated in Figures 31 to 34, with further specification and dimensions given in Appendix 2. This solution achieves CIRIA C736 compliance, including approaches for improving the sustainability of construction in the following ways:

- Bund height: calculated using the CIRIA 25/110 percent rule, divided by the area encompassing the bunded area not including the footprint of tanks, buildings, and other obstructions. Rainwater handling was also considered.

- Surge allowance: CIRIA C736 table 6.3 specifies the freeboard required to protect against surge.  Recognising these recommendations, an allowance of 0.25m for walling and 0.75m for earth works has been added to the bund heights to protect against surge.

- Drainage: all surface drainage infrastructure will be assessed during the design phase to confirm sufficient capacity is available to deal with rainwater falling into the bund.

- Walling: in-situ or pre-cast products are considered to allow for installation where space is limited and considers pre-existing walling as part of the installation.

- Earth works: non-engineered and engineered constructed earth bund materials are considered where space is available, this includes existing earth embankments. Where earth bunds are a preferred option, bentonite clay matting, concrete matting, or poured concrete will be used to produce an impermeable outer surface.

- Permeable areas: all permeable areas of land that could receive a spill will be made impermeable or protected by a bund.

- Ramps & flood gates: will be used as required to provide access into bunds.  Ramps are the preferred solution, as they provide access without affecting the integrity of the bund.  Floodgates may be installed where the need for access is very infrequent, and installation of a ramp is not practical.  Where floodgates are required an appropriate management system will be implemented to ensure an appropriate level of environmental protection is maintained when they are in use.

- Hardstanding areas: existing areas of hardstanding that will form part of the containment solution (in-situ concrete, access roads) will be assessed to ensure that they provide a level of containment consistent with the requirements of CIRIA C736.

YW have committed to install a containment solution that complies with CIRIA C736.  The current preferred design is shown below but may be subject to minor modifications and amendments during detailed design phase.

The total containment volumes required within the bunding was calculated as per Table 6. Following the CIRIA requirement to contain the larger volume of 110% of the largest tank or 25% of all tanks, a bund volume of 783 m3, 275 m3, 1,748 m3 and 968 m3 is necessary for sludge containment within the single tanks and multi-tank areas 1, 2 and 3.  An additional volume will be allowed for freeboard to handle surge (Appendix Table 1).

Table 6. Containment volume calculations.

| Tank | Area | Hydraulically linked to another tank? | Volume m3 (per tank) | Total volume m3 (group) | 110% size m3 |
| --- | --- | --- | --- | --- | --- |
| Digester feed tank | Single tank | NA | 712 | 712 | 783 |
|  |  |  | Largest 110% size |  | 783 |
|  |  |  | Total volume | 712 |  |
|  |  |  | 25% of total volume | 178 |  |
| Sludge import tank | Multi-tank area 1 | No | 150 | 150 | 165 |
| 2 liquor return balancing tanks |  | No | 250 | 500 | 275 |
|  |  |  | Largest 110% size |  | 275 |
|  |  |  | Total volume | 650 |  |
|  |  |  | 25% of total volume | 163 |  |
| 2 drum thickener feed tanks | Multi-tank area 2 | No | 1,589 | 3,178 | 1,748 |
|  |  |  | Largest 110% size |  | 1,748 |
|  |  |  | Total volume | 3,178 |  |
|  |  |  | 25% of total volume | 795 |  |
| 2 digesters | Multi-tank area 3 | Yes | 441a | 882 | 970.2 |
| 2 digested sludge storage tanks |  | No | 880 | 1,760 | 968 |
|  |  |  | Largest 110% size |  | 968 |
|  |  |  | Total volume | 2,642 |  |
|  |  |  | 25% of total volume | 661 |  |

Figures 31 to 34 show localised bunding solutions for single and multiple tanks. As access for operation is crucial for these tanks the bunds have incorporated road slopes and any existing site structures.  For example, a sloping hardstanding access road is utilised as containment, this is evidenced in Figure 33 where the road shows a significant gradient with a retaining wall adjacent to the tanks.

New bund wall

New impermeable surface

Existing wall

Figure 31. Mitigation - multi-tank area 1

New impermeable surface

Existing wall

Slope

New bund wall

Figure 32. Mitigation - multi-tank area 2

New bund wall

New impermeable surface

Figure 33. Mitigation - multi-tank area 3

New bund wall

New impermeable surface

Figure 34. Mitigation - digester feed tank

### Surge

The catastrophic collapse of a tank would lead to a rapid release of sludge which will then flow across the surrounding area.  This is particularly true on steep gradients, which will encourage flow to travel further.  As flow travels across flat ground, it will lose speed and the risk from surge will rapidly decrease.

Sludge released in this way will tend to flow over obstacles, but physics limits the height of barrier which it can pass.  It is possible, but complex to calculate the extent of flow over obstacles using specialist software, but it would be prohibitively expensive to do this for every site where containment is being considered.  In the absence of detailed modelling, CIRIA C736 provides guidance on the additional height of bund wall (Figure 35), above settled spill level, that is required to ensure surge flow does not pass containment walls.

Figure 35. Surge protection requirements.  Taken from CIRIA C736 pg 54.

Lundwood is a large site, with significant distances between assets.  It is also built on the sides of a hill, which means sludge has potential to travel a significant distance.  However, the velocity of flow is expected to be diminished because of its rheology and the significant areas of unmade, rough, ground.  Although there are open topped tanks at Lundwood, these are all a significant distance from sludge holding tanks and outside of bunded areas.  Recognising this, no additional surge protection is required outside of bunded areas.

### Jetting

The EA guidance on spills to permeable surfaces means YW has reconsidered its approach to jetting and recognises that surfaces which could receive a sludge spill because of tank failure will require an impermeable surface.  This means tank leaks, including jetting, within the tank locations at Lundwood will be contained as the immediate and surrounding surfaces will be made impermeable.

The risk of environmental harm as a result of jetting from these tanks has been assessed as low for the following reasons:

- YW design, construction and monitoring controls ensure tanks are constructed to a high standard and would identify any critical weaknesses at an early stage, and well before catastrophic failure occurred.

- For tanks constructed of concrete, the formation of a hole large enough to allow jetting, but small enough to avoid total tank collapse is unlikely.  If failure were to occur, it is much more likely to initially show as cracking, giving time to respond before significant sludge escaped.

  - A technical note has been provided in 0 confirming the failure mechanism of a tank constructed from concrete.

- The sludge in the concrete digesters is relatively viscous and this is likely to reduce the extent of jetting as viscous materials will travel relatively slowly through an orifice.

- The most likely cause, albeit it still very unlikely, of a tank wall puncture that would allow jetting is a direct impact, the most likely cause of which would be an out-of-control vehicle.  If this were to happen, it would almost certainly be at ground level.  In most cases, new bund walling and existing site structures will protect tanks from direct impact.

Yorkshire Water understand that while risk is low, consideration of jetting remains a requirement of CIRIA C736.

The blue circles in Figures 36 to 41 show areas which could be affected by jetting.  These have been calculated according to CIRIA C736 guidelines (Appendix Figure 2).

#### Multi-tank area 1

New bund wall

New impermeable surface

Existing wall

Figure 36 Jetting potential for multi-tank area 1

The import tank to the west of multi-tank installation 1 appears to present a risk of jetting, but in practice the high wall to the north of the tank will mitigate the risk of tank content passing over the wall, Figure 37.  During detailed design of the containment solution for this area, it will be confirmed that the wall height, and distance from the tank, provide full compliance with CIRIA C736.

There is also some risk of jetting passing over the eastern edge of the bund, but in practice it is likely that the final wall height will provide containment in line with CIRIA C736.  Again, this will be confirmed during detailed design.

Figure 37 View from elevated ground to the north of the import tank

#### Multi-tank area 2

Figure 38 Jetting potential for multi-tank area 2

Multi-tank area 2 contains two large, steel, thickener feed tanks.  Initial analysis shows that potential jetting from the more westerly tank will be entirely captured within the bunded area.  The easterly tank has potential for jetting to pass over the bund wall.  Note that the land rises in this direction, during detailed design YW commit to either installing jetting protection in this area and/or extending the bund up the existing bank to ensure potential jetting is captured on an impermeable surface.

Figure 39 - Land rises to east of thickener feed tanks

#### Multi-tank area 3

Figure 40 Jetting potential for multi-tank area 3

Multi-tank area 3 includes the digesters and the digested sludge balance tanks.  All tanks are constructed of concrete and as discussed previously; the failure mode of concrete tanks makes jetting very unlikely.  Notwithstanding this and recognising the EA preference for modelling of jetting in line with CIRIA C736, see image above.  CIRIA aligned analysis of jetting from the digesters is complex, as the tanks are partially set into the ground, with ground level altering around the circumference of the tank.  As shown in the image above, based on current data, jetting from all tanks in this area will largely be capture within the

#### Digester feed tank

Figure 41 Jetting potential for digester feed tank

The digester feed tank is of concrete construction and is extremely unlikely to fail in a way that leads to jetting, see engineer’s note (Appendix 3).  If an analysis in line with CIRIA C736 is completed, the potential risk of jetting passing the bund wall to the west and south of the tank can be seen.   As additional protection, to the west, the existing building will provide a degree of containment, and during final design of the bund it will be confirmed that any tank content reaching this wall will be ultimately contained within the bund.

## CIRIA C736 compliance and construction.

The secondary containment solution at Lundwood will be implemented by contractors chosen via YW’s procurement process.  This process is designed to ensure contractors have the knowledge and experience to build a secondary containment solution that complies with CIRIA C736.

The effectiveness of the containment and jetting solution will be confirmed by the appointed construction company, who will use the bunding design described in this document as a starting point for development of detailed design. YW will confirm that the final bunding solution is acceptable to the EA prior to commencement of the build.

# Preventative maintenance and inspection regime

## Above ground tanks

All tanks are tested and inspected as part of initial construction quality assurance checks; an example of a tank check is shown in Appendix 5.

The tanks at Lundwood are regularly inspected by a qualified engineer. As part of these inspections, the reinspection period of each tank will be determined by the inspection engineer (anywhere from 6-months to 3 years depending on the condition of the tank). Any defects identified during inspections will be actioned and remedial works carried out as soon as possible.

Visual checks on tanks also form part of daily/weekly operational checks.  These ensure that any damage or major degradation of tanks is identified as a risk and is reported before a hazard can develop.

## Below ground level tanks/chambers

- Yorkshire Water understand the environmental risk associated with underground structures and are committed to identifying and rectifying any leaks from them.  To support this aim, YW commit to the following:

- Daily visual inspection (Mon-Fri on certain sites) of subsurface tanks, wells, and surrounding ground by site operational team.  These checks will identify major structural issues visible above liquid/ground level and any changes in ground conditions.

- Monthly external visual inspection of subsurface tanks, wells, and surrounding ground by a technically competent manager.

- Risk assessed additional monitoring.

- Three monitoring techniques have been identified as potentially appropriate for subsurface tanks/chambers identified as high risk.

  - Drop testing - the chamber/tank will be filled to normal maximum operating level, covered to prevent loss by evaporation, and left for 24 hours.  For each tank an acceptable drop in level will be specified, if this is passed during the test, a repair will be completed.

  - Empty and inspect – tanks will be emptied, cleaned and a visual inspection completed.

  - Borehole monitoring – sampling of up- and down-hydraulic gradient boreholes located around a tank perimeter will allow leaks from the tank to be detected and investigated as required.  Following an initial period of monitoring to establish a baseline, trigger levels will be set and agreed with the EA.

- Repair timescales.

  - Where a leak is detected using any of the above techniques, YW will isolate the source of the leak e.g., empty or bypass the tank as soon as practicable.  The tank will not be returned to service until a repair has been completed.

- The use of inlet/outlet flowmeters to detect leaks has been considered, but the large volumes of flow passing through pipes combined with accuracy limitations of the instrument mean that leaks are likely to have already had an environmental impact, visible at ground level, by the time they are large enough to be detected.  On this basis YW do not consider flow comparison to be a useful tool for leak detection.

## Underground pipes

To mitigate the risk of failure of underground pipework, e.g., cracks and splits, surveys are completed using in-pipe crack detection technology every 5 years if mechanical joints are present, and 10 years if they are not. For future pipe installations, underground pipework will be avoided.  Where this is not possible, pipes will be installed with secondary containment and leak detection.

In the event of an incident/ accident a team will be deployed immediately to isolate the damaged pipe and a spill management procedure will be followed. Thereafter, repairs to the damaged pipework will be arranged. Additionally, the incident will be logged, and hazard assessed to reduce or eliminate the risk of occurrence.

## Impermeable surfaces

Appropriate containment of potential spills in large part relies on capturing them on impermeable surfaces that protect underlying ground.  At Lundwood these surfaces are typically made of concrete and YW are committed to keeping these in good condition to ensure that any potentially polluting liquids cannot pass the impermeable layer.  The most likely path for liquids is through cracks and other damaged areas.

Responsibility for monitoring the condition of impermeable surfaces sits with two roles within YW.

- Site operators will carry out daily visual inspection of impermeable surfaces as part of their normal duties.

- The Technically Competent Manager (TCM) with responsibility for the site will carry out a monthly inspection of impermeable surfaces.

Where damage is identified a high priority job will be raised for repairs to be completed through the YW reactive maintenance system.  In cases of severe damage, temporary protection will be installed around the damaged area to ensure that effective liquid capture is maintained.

# Implementation and timescales

## Construction

A plan outlining the implementation of containment solutions identified is shown in Table 7. The timescales and estimated dates are indicative, and subject to timely external contract appointment, including acceptance of the procedures and ideal weather conditions for construction. Furthermore, bottlenecks, such as resource availability due to ongoing number of installations has not been factored in. These will be revisited once contractors are appointed, and capacities understood.

Table 7. Secondary containment implementation stages and schedule.

| Stage | Estimated date complete |
| --- | --- |
| Completed detailed final design | 1st March 2024 |
| Commence construction | Autumn 2024 |
| Complete construction | March 2025 |

# Conclusions and recommendations

- This study has considered the risks associated with CIRIA C736 defined loss of containment scenarios at Lundwood STF.  This assessment was completed using a source-pathway-receptor model. A computational modelling study has been undertaken, which adopted conservative assumptions to understand a worst-case scenario for the spread of spills. A computational modelling study has been undertaken, which adopted conservative assumptions to understand a worst-case scenario for the spread of spills. This enabled the potential effects of a substantial, unmitigated loss of containment to be considered; this has shown that further mitigation is required to protect sensitive receptors (the metric of compliance being an equivalence to a traditional 25 / 110 per cent capacity secondary containment bund in line with CIRIA C736 via the ADBA study).

- The need for additional secondary containment infrastructure has been confirmed and YW commit to installing this. YW also understand the following factors and existing mitigation measures should be maintained to ensure an appropriate level of environmental protection:

- Current controls

- Continuation of the measures already in place to minimise the likelihood of catastrophic failure of sludge vessels, through the use of stringent technical standards, SCADA technologies and regular visual inspections.

Existing infrastructure

    - Site drains are able to return liquid to the inlet works for treatment, providing containment and flow mitigation.

    - The sludge cake storage and loading pad has been engineered to drain liquid contents which returns to the inlet works of the WwTW, acting as remote containment.

    - In some areas spills, leaks and catastrophic pipe failures the site surfacing and drainage would transfer liquid to the WwTW, which would contain and minimise potential effects of loss of containment.

Reducing Likelihood

    - Whilst the potential for catastrophic tank failure can never be wholly mitigated when sites are operated with large tank inventories, the likelihood of substantial failure is very low, as evidenced by YW’s own track record of operating sludge storage/treatment vessels across its asset base.

    - In support of likelihood of failure YW has reviewed actual failure data. YW has over 40 years of experience in operating AD plants and STF’s. YW has 14 AD sites, 5 of these sites have Environmental Permits. Within this time YW has not experienced the catastrophic collapse of a storage vessel.

    - YW has found from experience that ‘failures’ of concrete tanks are generally associated with ancillaries such as joints, waterstops, seals, etc, rather than any inherent defect with the actual civil structure. YW has experienced one incident of note, and this was at Hull STF digester number 5. This example is a case in point; the release of sludge that occurred was caused by the failure of a ‘link seal’ mechanical coupling that should have provided a watertight seal around the outside of a mixer pipe intrusion.  In comparison with a catastrophic collapse scenario, this resulted in relatively controlled spill of small volume.

Environmental impact

Receptors in the area must be protected from the effects of major sludge spills to reduce pollution and impacts to biodiversity.

# ARUP Design Overview

The Stantec containment outline, as described in Section 4, was 	passed to Arup for detailed design.

The design of the secondary containment has been developed to standards as set out in the *establishing best available techniques (BAT) conclusions for waste treatment, under Directive 2010/75/EU of the European Parliament and of the Council” document; specifically, BAT 19c and 19d. The design proposals for the site have been developed to be compliant with the recommendations and best practice set out in CIRIA C736. The secondary containment proposals at Lundwood have been developed to contain sludge tanks in bunded areas within the site. The Tuflow modelling was carried out and can be seen in Secondary Containment Lundwood Maximum Containment Depth Sheet (appendix 6).

The secondary containment design will involve bunds within the installation area that will act as a physical barrier, preventing any sludge from escaping the designated areas. The defence shall include containment walls. The design also includes resurfacing the bunded areas to ensure the ground impermeability within the containment area. This will effectively prevent any seepage or penetration of sludge into the surrounding soil. The design includes, where appropriate, alterations to the existing drainage and utility infrastructure. These modifications are necessary to redirect any potential spillage or leakage of inventory to the designated containment systems.

As the secondary containment design is being retrofitted, there are elements of the CIRIA 736 guidance which cannot be achieved. In these instances, an alternative measure will be implemented to achieve an equivalent standard to provide the same level of environmental protection.

Surface Water Drainage

The site benefits from an existing drainage system which will be used as part of the design. The design will be used to manage surface water accumulating within the containment area.

Ciria C736 dictates that a new site would have a fully bunded and blind drainage system. This is difficult to retrofit on an existing site. YW is proposing an alternative level of protection would be to install new drainage (where necessary) to accommodate the increase in surface water that will be created by the additional impermeable surface area. A gate valve (or similar) would be provided to enable the bund to be isolated in the event of a spill. It would remain open as standard.

Furthermore, Ciria C736 states the bund should be sized to accommodate a 10% AEP 24 hour storm event preceding a spill incident and an 10% AEP 8 day event following an incident. This would require a significant storage vessel for rainwater. As described previously, the bund would be maintained in an empty state up until the point of a spill event. Therefore YW is proposing to retain the AEP 8 day volume post spill but remove the 10% AEP 24hour storm event volume.

Impermeability

Ciria c736 states the replacement of permeable areas with impermeable surfaces and directs the use of reinforced concrete pavements for class 1-3. Ciria c736 requires a clay liner under concrete. This existing site was not designed with a clay liner situated underneath the existing concreted areas.

YW is proposing that existing concrete and paved areas within the installation bund will not be lifted to replace with a clay liner. To lift the existing surfaces would result in many tonnes of waste material. It’s proposed we would retain existing flexible pavements (concrete and tarmac) and undertake repairs to ensure surface integrity where needed. Permeable liners would be installed on the current landscaped area with drainage at the base. It’s proposed a clay liner would not be required under this liner.

# Appendices

- Appendix 1 - ADBA assessment tool

Screenshot from spreadsheet containing full assessment.  Full document included as part of permit submission.

Extract

Appendix Figure 1. ADBA spreadsheet screenshot

- Appendix 2 - CIRIA C736 compliant solution

Appendix Table 1.  Lundwood bunding solution design specification and dimensions.

| Category | Criteria | Unit | Value |
| --- | --- | --- | --- |
| Multi-tank area 1 -import |  |  |  |
| Design specification | CIRIA C736 spill volume [25/110%] | m3 | 275 |
|  | Bund perimeter length | m | 137 |
|  | Total containment surface area | m2 | 741 |
|  | Maximum Final Spill depth | m | 0.37 |
| Bunding requirements | Concrete bund height | m | 0.62 |
|  | Total concrete wall length | m | 137 |
|  | Earth bund height | m | n/a |
|  | Total earth bund length | m | n/a |
| Existing bunding | Existing concrete walling length | m | 62 |
|  | Existing earth works length | m | 0 |
| Build required | Required concrete walling length | m | 75 |
|  | Required earth works length | m | 0 |
|  | Impermeable surfacing area | m2 | 639 |
|  | Trief kerb length | m | 0 |
| Multi-tank area 2 – thickener |  |  |  |
| Design specification | CIRIA C736 spill volume [25/110%] | m3 | 1748 |
|  | Bund perimeter length | m | 223 |
|  | Total containment surface area | m2 | 2606 |
|  | Maximum Final Spill depth | m | 0.67 |
| Bunding requirements | Concrete bund height | m | 0.92 |
|  | Total concrete wall length | m | 188 |
|  | Earth bund height | m | 1.42 |
|  | Total earth bund length | m | 35 |
| Existing bunding | Existing concrete walling length | m | 74 |
|  | Existing earth works length | m | 30 |
| Build required | Required concrete walling length | m | 114 |
|  | Required earth works length | m | 5 |
|  | Impermeable surfacing area | m2 | 1496 |
|  | Trief kerb length | m | 0 |
| Multi-tank area 3 |  |  |  |
| Design specification | CIRIA C736 spill volume [25/110%] | m3 | 968 |
|  | Bund perimeter length | m | 251 |
|  | Total containment surface area | m2 | 3616 |
|  | Maximum Final Spill depth | m | 0.31 |
| Bunding requirements | Concrete bund height | m | 0.56 |
|  | Total concrete wall length | m | 183 |
|  | Earth bund height | m | 1.06 |
|  | Total earth bund length | m | 68 |
| Existing bunding | Existing concrete walling length | m | 0 |
|  | Existing earth works length | m | 68 |
| Build required | Required concrete walling length | m | 183 |
|  | Required earth works length | m | 0 |
|  | Impermeable surfacing area | m2 | 2009 |
|  | Trief kerb length | m | 0 |
| Digester feed tank area |  |  |  |
| Design specification | CIRIA C736 spill volume [25/110%] | m3 | 783 |
|  | Bund perimeter length | m | 120 |
|  | Total containment surface area | m2 | 3749 |
|  | Maximum Final Spill depth | m | 0.21 |
| Bunding requirements | Concrete bund height | m | 0.46 |
|  | Total concrete wall length | m | 120 |
|  | Earth bund height | m | n/a |
|  | Total earth bund length | m | n/a |
| Existing bunding | Existing concrete walling length | m | 0 |
|  | Existing earth works length | m | 0 |
| Build required | Required concrete walling length | m | 183 |
|  | Required earth works length | m | n/a |
|  | Impermeable surfacing area | m2 | 605 |
|  | Trief kerb length | m | 0 |

- Appendix 3 - Structural integrity note for concrete tanks

- Appendix 4 - CIRIA C736 jetting calculation

Appendix Figure 2. CIRIA C736 jetting calculation to determine jetting solution.

- Appendix 5 - Example tank inspection report

Appendix Figure 3. Example equipment inspection report

- Appendix 6 - (Arup) Secondary Containment

CIRIA (2014) Containment systems for the prevention of pollution: Secondary, tertiary, and other measures for industrial and commercial premises (C736; 2014)