# Fire prevention plan

Plan version:	4
Date of plan:	13/04/2023
Site details
Site name:	William Rowland
Site address:	Unit 4. Enterprise Way. Tankersley. S75 3DZ
Operator name: William Rowland
Company Number: 00853661
Who this plan is for
This plan is for staff, fire officers, visitors, and contractors working on site.
Site Address: William Rowland, Unit 4. Enterprise Way. Tankersley. S75 3DZ
 Site Operator: William Rowland
CONTACT DESCRIPTION OFFICE HOURS OUT OF HOURS:
Richard Lowe 07740 408776,
Steve Biggerdike 07718 488467,
Bob Clark 07522 236121.

Barnsley Hospital,
Gawber Road. Barnsley. S75 2EP
NHS Direct 0845 4647

South Yorkshire Police
Churchfield sub divisional office. Barnsley. S70 2DL
0114 220 2020, 999.

Tankersley fire station
Maple Road, Tankersley S75 3DL.
01142727202, 999.

Environment Agency
Quadrant 2 99 Parkway Avenue,
Sheffield, S9 4WF,Tchale Lymer,03708506506.

Barnsley Metropolitan Borough Council
Lobwood, Worsbrough Bridge,
Barnsley S70 5EP.
01226 289096.

Yorkshire Water.
Mains water and
sewerage supplier
Business Stream 0330 123 2000

1.1 Fire Prevention Objectives
This Fire Prevention Plan has been designed to meet the following 3 objectives:
• To minimise the likelihood of a fire happening;
• To aim for a fire to be extinguished within 4 hours;
• To minimise the spread of a fire within the site and to surrounding neighbouring sites. All site staff and contractors must be aware and understand the contents of the Fire
Prevention Plan (FPP) and what they must do during a fire.
This FPP document will be kept in the site office.

Contents

Fire detector/alarm installation cert ………………………………………………………… 17
DX Connexion fire panel data sheet………………………………………………………... 17

## Types of combustible materials
## Combustible waste
- ferrous metal filings and turnings EWC 12.01.01
- non-ferrous metal filings and turnings EWC 12.01.03
- ferrous metal EWC 16.01.17
- non-ferrous metal EWC 16.01.18
12.01.01, 12.01.03, 16.01.17 and 16.01.18 (combined) could be in the region of a mixed maximum capacity 100MT and mixed quantities of each at any one time this is due to purchasing what is available on the market, at an average bulk density of 0.91 the total volume of the combined above wastes listed will be in the region of 109.89M³. This will be stored in either bulk bag, skip and or drums at varying weights but each individual container will not exceed 1.8M³ and not weighing greater than 1200Kg. An individual weight per code cannot be determined as to what is bought, processed and sold at any one time may vary.
### Other combustible materials
All other waste non-combustible.
## Using this fire prevention plan
### This fire prevention plan is available to all staff, fire officers and contractors, and visitors working on site and a copy is kept in the main office. A test of this fire prevention plan will be conducted every 12 months and recorded by the manager. In cases of a fire this plan must be adhered. To prevent any fire starting, the following actions must be followed;
- Ensure all plasma cutters are turned off and area is free from ‘hot’ materials.
- Integrity of the electrics are checked every 12 months.
- Removal of flammable materials such as wood, paper, packaging etc to storage.
- Regular maintenance of firefighting equipment by qualified technician
- Location of firefighting equipment displayed clearly as per fire risk assessment.
- All employees familiarised with emergency action and evacuation plan.
### Where the plan is kept and how staff know how to use it
The fire prevention plan will be stored in the main office and is accessible to staff, fire officers, contractors and visitors working on site at all times.
### Testing the plan and staff training
Training of staff will be carried out so that they understand the fire prevention plan and its contents. Contractors will be given instruction and guidance on the fire prevention plan and where it is located on their inductions to site. Testing of the fire prevention plan will be every 6 months and recorded by the manager in charge. All staff are fire extinguisher trained with several fire marshals (names and photo’s are displayed around site)
## Fire prevention plan contents
### Activities at the site
The main activity at the site is the cleaning of metals.
- Sorting and processing scrap metals by means of cutting and sizing.
- Using guillotines and shears to cut nickel, copper and aluminium to customer size and re-packing of merchanted metal powders, alloys and other materials for despatch.
- Degreasing using aqueous detergent to clean non-ferrous/ferrous swarf.
- Crushing and sizing of non-ferrous swarf by means of a pulveriser (hammer mill).
- Metals processed at this site are;
- Stainless steel alloys (austenitic/duplex/martensitic)
- Alloy/carbon/mild steel
- Nickel alloys
- Cobalt / chrome alloys
- Cobalt alloys
- Molybdenum
- The above metals are non-combustible.

### Site plan
The site is a new development of 4 units and is just 36 months old.

Receptor in bunded area for effluent (see attached drawing)

Drainage system for yard (turning circle/quarantine) area (see attached drawing)

## Manage common causes of fire (ignition sources)
### Arson
The site is covered and monitored by CCTV cameras (see attached certificate), controlled access to site, perimeter fencing which is protected with barbed and razor wire and also has an intruder and fire alarm which are also monitored 24/7.
CCTV, Fire and intruder alarm monitored by First county monitoring. Contact details 01757 244445.
In the event of an occurrence the following shall be contacted;
Taybar, key holders (24/7 service) 01226 288886.
Bob Clark 07522236121, Operations manager.
Gary Clarke, Production manager 07903 710218.
Adrian Tazzyman, logistics manager, 07903 710220.
### Plant and equipment
On site we use 6 x electric powered forklift trucks, 1 x 360 excavator diesel powered and 3 x jib hoist cranes along with vacuum lifting attachments. These items are maintained and have regular service intervals as set out in the LOLER and PUWER regulations.
### Electrical faults including damaged or exposed electrical cables
#### Electrics certification
As this is a new build it is currently covered by the fixed wiring regulations.
#### Electrical equipment maintenance arrangements
All electrical, non-fixed, is PAT tested annually, see attached certificates.
### Discarded smoking materials.
#### Smoking on site policies
The site operates a no smoking on site policy.
### Hot works safe working practices
Plasma cutting is done in a controlled area by trained operators only. The LEV system for the process has a spark arrester and detection built in.
Hot works are carried out under ‘authorisation to work permits’ which have sections on compliance with hot working.
### Industrial heaters
#### Use of industrial heaters
There are no industrial heaters in the working area.
### Hot exhausts and engine parts
#### Fire watch procedures
Hot exhausts from the plasma cutting process are extracted through an LEV which has spark arresters and detection built in, the checking of these exhausts form part of the check sheets.
### Ignition sources
Pallets are stacked and stored away from the building, other combustible items and waste packaging is stored in the designated skip for disposal.

Batteries in ELVs
Not applicable, end of life vehicles are not stored/processed on our site
### Leaks and spillages of oils and fuels
Leaks from the process are covered in the ‘process risk assessment’.
Chemicals for the cleaning process of the swarf is stored on a bunded pallet.
Cutting fluid is used in processing scraps on the bandsaws. This fluid is stored on a bunded pallet.
The outside yard is bunded with an oil and water separator which is alarmed.

### Build-up of loose combustible waste, dust and fluff
This section is not applicable as no waste dusts or fluffs are generated in our processes
### Reactions between wastes
Wastes are kept separate from each other both storage and for disposal
### Deposited hot loads
This section is not applicable as our process does not generate hot loads

## Prevent self-combustion
General self-combustion measures
The waste stored on site is not self-combusting waste.
### Manage storage time
#### Method used to record and manage the storage of all waste on site
A contract collection is in place with a registered collection agency for specific wastes (eg cardboard, general. Wood and metal skips). The contractor is informed for the collection when the skip is nearly full. These collections are every 2 weeks for general waste, 4 weeks for wood and cardboard, and 10 weeks for waste metal
Waste effluent is stored in IBC’s in a specific bunded area. When a load (@6 to 16 IBC’s) is achieved a registered waste contractor is contacted for disposal. This effluent build up is determined on how ‘dirty’ the material is being processed, but usually between 3 to 5 weeks.
The waste swarf is controlled by the in house computer software which monitors slow moving materials (after 3 months they are slow moving and after 6 months they are actioned for sale). The swarf when processed is the product that we sell, therefore monthly stock meetings are held to determine the stock positions. If stock hasn’t been actioned by 6 months then a plan is drawn up to sell the product and rotate stocks.
All the above wastes are non-self-combustible materials.
#### Stock rotation policy
Swarf for cleaning is delivered to the site and undergoes a testing process to ensure what we have had delivered is what we have actually bought. The swarf is then put on the system and is cleaned in a ‘family alloy’ process. When the material has gone through the process the cleaned swarf is then a saleable product and is offered out to customers. Internal computer software monitors date of purchase to ready for sale and slow moving stocks. These stocks are discussed in the monthly stock meetings.
### Monitor and control temperature
#### Reduce the exposed metal content and proportion of ‘fines’
This section is not applicable as these processes are not used.
#### Monitoring temperature
The cleaning process is temperature controlled to a maximum detergent temperature of 70ᵒC
#### Controlling temperature
When the temperature of the process exceeds the 70ᵒC limit the machine will trip out and alarm.
#### Dealing with hot weather and heating from sunlight
This section is not applicable as the items stored as waste are controlled by volume.
Waste bale storage
This section is not applicable as there are no waste bales stored on site.
## Manage waste piles
#### Maximum pile sizes for the waste on your site
Other combustible wastes on site include.
- 20-yard waste cardboard skip, 15.01.01 and 20.01.01
- 20-yard waste wood skip,
- 20-yard waste plastic, 15.01.02 and 20.01.39
A contract collection is in place with a registered collection agency for specific wastes (eg cardboard, Wood and metal skips). The contractor is informed for the collection when the skip is nearly full. These collections are every 2 weeks for general waste, 4 weeks for wood and cardboard, and 10 weeks for waste metal
The wooden pallets to be sufficient for 1 month’s repacking/distribution which may be 75 euro pallets, 50 4 way pallets and 50 standard pallets. These are stored away from the building.
The IBC containers for the effluent waste from the process will only comprise a maximum of 16 at any given time and will only be stored in the bunded area for pumping out and disposal of an accredited waste carrier.
Waste ferrous and non-ferrous turnings are rotated as per production requirements and are controlled by slow moving stock meetings.
The metal waste (swarf) will be stored inside the building in either bulk bags, skips and/or drums for security reasons. There could be a maximum of 100MT at full capacity which is rotated by production requirements and may not drop below 45MT (processing requirements). There will be a constant supply of swarf for the process but rotated accordingly.

#### Procedures for storage of end-of-life vehicles
This section is not applicable as no end-of-life vehicles are stored.
### Waste stored in containers
Types of containers you are using
There are 6 skips on site, 2 capable of holding 6 cubic metres (1 for general waste and 1 for used bulk bags), 1 capable of 20 cubic meters for waste metal, 1 capable of 20 cubic meters for waste wood, 1 capable of 20 cubic meters for plastic 15.01.02 and 20.01.39 and 1 capable of 20 cubic meters for cardboard 15.01.01 and 20.01.01.
Skips are situated 6 meters away from buildings.
Waste from the cleaning process is stored in IBCs in the bunded area to a maximum of 16.
Waste metal swarf contained in either bulk bags, metal skips and/or drums will be stored inside for security purposes and separated from other combustibles.
Metal swarf maximum capacity is 109.9M³ and stored in either bulk bags, skips and/or drums.

Accessibility of containers
All the skips are in the main yard which is accessible through a controlled gate from Enterprise Way.

Moving containers in a fire
All skips are sited away from all buildings and would not be required to be moved in a fire.
## Prevent fire spreading.
Separation distances
Pallets, cardboard, general waste and IBC’s are stored in the main yard and are kept separate. Metal wastes can be moved by FLT.

Fire walls construction standards
Metal swarf is segregated from all other materials and 3m away from building perimeter, there are no Internal walls, or bays within the buildings, apart from the offices.
Storing waste in bays
This section is not applicable as no waste is stored in bays.
## Quarantine area
Quarantine area location and size
Metal swarf (waste) is stored inside the building in a designated area opposite the cleaning machine on the internal North face of the building. If a parcel (1.8M³ maximum volume) did set on fire, then this would be taken out into the yard for quarantining in one of two area’s designated on the attached site plan as ‘Turning Circle’. Each turning circle is 490M². temporary barriers are readily available to stop and warn traffic, employee’s and visitors of the hazard. Each parcel can be transported to these area’s for quarantining until the building is cleared. Area required is 100MT/1.2MT (max weight of individual parcel) = 84 parcels x 1.44M² (area of each parcel) = 120.96M² for 100MT. at 500Kg a parcel the area required to quarantine 100MT would be 288M².

#### How to use the quarantine area if there is a fire
The metal swarf is segregated from all other materials and is a minimum of 3m away from the building perimeter in open air and can be barriered off for isolation in the yard by means of temporary barriers and fire watchers. Employees are trained and briefed and with onsite fire marshals.

#### Procedure to remove material stored temporarily if there is a fire
Any materials stored are usually stored on pallets, these could be moved by fork lift truck.
#### Detecting fires/systems in use

Apollo XP95 complies with BS EN54 and certified by LPCB
The fire alarm system is an automatic system for detection of fire by use of detectors for both smoke and heat. Manual call points are provided at fire exit door locations. The system functions 24 hours a day permanently.
The XP95 optical smoke detector uses an integral LED and a photo diode at an obtuse angle. The XP95 heat detector monitors temperature by using a single thermistor which provides a voltage output proportional to the outside air temperature. The combined inputs from optical and heat sensors are processed by using a sophisticated algorithm.
The fire detection system in place is monitored 24/7 along with internal and external CCTV
The CCTV/fire alarm systems are annually serviced, fire alarm checks are done weekly and there is an annual fire drill.
See appendix 1 for installation certificate and panel data sheet

#### Suppression systems in use

A fire risk assessment has been completed by an accredited contractor and adequate firefighting equipment has been positioned according to the assessment. The fire extinguishers are the only suppressant for dealing with a fire which are 9 x 6Kg dry powder, 13 x 6 Ltr Afff, 10 x 2Kg CO2, 1 x 2Kg powder and 1 x fire blanket as per fire risk assessment. There is no sprinkler system on site. The site has a 24/7 key holding service provided by a local security company who are contacted by the monitoring service in the event of intruder alarm, CCTV and/or fire alarm activations out of normal working hours.
The fire extinguishers present on site are subject to an annual service, fire alarm and CCTV are on a service contract.

Active firefighting
Access to the site is from a controlled gate which opens automatically on the fire alarm activation which allows entry to the fire service if necessary.

Also all staff members are fire extinguisher trained and trained fire marshals, in the event of a fire, staff would attempt to extinguish the fire using hand held fire extinguishers, dry powder and CO2, these have been deemed suitable and sufficient by the fire risk assessment.
## Water supplies
### Available water supply
The nearest fire hydrant is situated on Enterprise Way and is 2 metres from the office gate.
It is a requirement that Yorkshire water provide an unlimited supply of water to fire hydrants at 1200l per minute.

Show the calculation for your required water supply

Waste swarf (assuming maximum 100MT) with an average bulk density of 0.91 = 109.9M³
Maximum pile volume in cubic metres	Water supply needed in litres per minute	Overall water supply needed over 3 hours in litres	Total water available on site in litres
Maximum capacity = 109.9M³	732.96 litres per minute / = 0.732M³	131,933 litres	Unlimited water is available by means of a fire hydrant, with a water pressure of 3bar, rising to 5bar through a 100mm outlet valve.

The waste stored on site does not constitute a volume sufficient as to require a 3 hour supply. The above calculation is based on a 1200l per minute supply as detailed in water supply to small industrial sites.
Water supply for 3 hours (1.2M³ x 60 minute x 3 hours) = 216M³
Water supply required for maximum capacity (0.732M³ x 60 minutes x 3 hours) = 131.7M³
## Managing fire water
Containing the run-off from fire water
The site has 2 underground oil/water separators which are alarmed and a bunded area with an oil/water collector of 12M³ which has also got a full level alarm.
If a parcel (maximum volume 1.8M³) caught fire then 1.5 minutes of water would be required to suppress the fire which would be 1800 litres (1.8M³). if the maximum capacity was to set on fire then the run off water will have to travel 75M (with a width of @70M) to reach the drainage system which is at the base of a slight incline running towards the bund. There are also wet vacuum cleaners that can vacuum the fire water and discharge direct into IBC’s for collection and disposal.
## During and after an incident
### Dealing with issues during a fire
All staff are fully fire trained, and fire Marshalls are in place, they could communicate with the fire brigade, and supply the necessary information. There is a fire ‘grab bag’ in place for the fire brigade.

### Notifying residents and businesses
Due to the small size and nature of the waste stored on site, it is envisaged that any fire would not have a detrimental impact on any nearby residents and businesses other than the airborne smoke. With 24/7 monitoring of CCTV, intruder and fire alarm and also 24/7 keyholding service and the fire brigade in close proximity of our site a fire can be detected early and dealt with swiftly making the impact a low risk. Residents and neighbours can be contacted verbally on foot/in car and through telephone/email contacts.

### Clearing and decontamination after a fire
If a recovery procedure is required, the operator would instigate the following;
a) Remove damaged material to a permitted facility that is able to deal with it legally.
b) Ask engineers to carry out repairs on any plant, vehicles and/or infrastructure.
c) Assist the FRS with the fire investigation and where necessary engage the advice from
a professional fire consultant.
d) Review the FPP and EMS procedures and improve upon where found deficient.
e) Review training requirements for staff.
f) Assess whether further preventative measure could be implemented.
g) Ensure all fire equipment, where used, is replenished.
h) Remove fire water to a permitted facility for disposal.

### Making the site operational after a fire
The procedures in the above section cover this section.

Above is the Fire Prevention Review

Above is the authorisation to work permit

Appendix 1.