## 1-EmPar
Emissions Parameters for Dispersion Model
|  | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | A10 | A11 | A12 | A13 | A17 | A18 | A19 | A20 | A21
Parameter | Units | Boiler 2 | Boiler 3 | Boiler 4 | Boiler (AM) 1 | Boiler (AM) 2 | Boiler (AM) 3 | Building 7 - Generator 1 | Building 7 - Generator 2 | Building 2 - Generator 1 | Building 1 - Generator 2 | Building 27 - Generator 1 | Building 5 - Generator 1 | Building 5 - Generator 2 | Building 2 - Generator 3 | Building 9 - Generator 1 | Building 9 - Generator 2 | CHP Engine 1 | CHP Engine 2
Building | - | Building 7 | Building 7 | Building 7 | Building 8 | Building 8 | Building 8 | Building 7 | Building 7 | Building 2 | Building 34 | Building 27 | Building 5 | Building 5 | Building 64 | Building 9 | Building 9 | External | External
Supplier & Model | - | Dunphy TD530YMLVPRT5C Burner | Dunphy TD525ZMLVPRT5C Burner | Dunphy TD525ZMLVPRT5C Burner | Econoflame Type 132, Code 858-2, Year 1994, S/N: 024054 | Econoflame Type 132, Code 858-2, Year 1994, S/N: 024052 | Econoflame Type 132, Code 858-2, Year 1994, S/N: 024053 | GEC Dorman Diesels, Engine type 12STCA(R3), No. 12132/0785/007, 1500 RPM, 1,136 BHP, 847 kW | GEC Dorman Diesels, Engine type 12STCA(R3), No. 12132/0785/007, 1500 RPM, 1,136 BHP, 847 kW | Scania 5Y9XL15 6BDB, Engine DC16 45A, 15.6L V*, 536HP@1500RPM | Cummins 33122005, Type KTA/50/G3, 1,645HP @ 1500 RPM | GEC Dorman Diesels, Engine type 12STCA(R3), No. 12132/0681/003, 1500 RPM, 1,136 BHP, 847 kW | Cummins KTA50-G1, 1,300HP@ 1500 RPM, 1,015kVA | Cummins KTA50-G1, 1,300HP@ 1500 RPM, 1,015kVA | Cummins KTA38-G2 980HP@1500RPM, 825kVA | MTU Diesel Engine 12V 4000, 1,420kW @ 1500RPM | MTU Diesel Engine 12V 4000, 1,420kW @ 1500RPM | - | -
Engine Datasheet | - | bar: A1 to A8; A10 to A17; A20 to A21
Notes on Datasheet | - | - | - | - | no data available. <250mg/NM3 or <5MWth? | no data available. <250mg/NM3 or <5MWth? | no data available. <250mg/NM3 or <5MWth? | scaled from Scania | scaled from Scania | Stage II 6g/kWh | scaled from MTU | scaled from Scania | scaled from MTU | scaled from MTU | scaled from Scania | 10g/kWh | 10g/kWh | - | -
Long- or Short-term Modelling | - | Both | Both | Both | Both | Both | Both | short | short | short | short | short | short | short | short | short | short | Both | Both
Exhaust details
Fuel used | - | gas and oil | gas and oil | gas and oil | gas | gas | gas | oil | oil | oil | oil | oil | oil | oil | oil | oil | oil | gas | gas
Previous Modelling Completed | - | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | no | no | no | yes | yes
Emissions Tested in Factory / Onsite? | - | - | - | - | - | - | - | - | - | yes | - | - | - | - | - | - | - | - | -
Stack Internal Diameter | m | 0.74 | 0.61 | 0.51 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Stack Orientation | - | vertical | vertical | vertical | vertical | vertical | vertical | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical | vertical | horizontal | horizontal | vertical | vertical
Stack Height | mAG | 35 | 35 | 35 | 3 | 3 | 3 | 8 | 8 | 12 | 5.5 | 7 | 2 | 2 | 8 | 3 | 3 | 25 | 25
Stack Area | m2 | 0.43014 | 0.29228 | 0.20431 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.03142 | 0.19637 | 0.19637
Exhaust Temperature | °C | 210 | 198 | 214 | 180 | 180 | 180 | 462 | 462 | 462 | 463 | 462 | 463 | 463 | 462 | 463 | 463 | 100 | 100
Efflux Velocity | m/s | 14.9906 | 14.9901 | 14.9909 | 15 | 15 | 15 | 0.1 | 0.1 | 0.1 | 107.5501 | 91.3439 | 94.2666 | 94.2666 | 78.8002 | 0.1 | 0.1 | 16.2954 | 16.2954
Volumetric Release (actual) | m3/s | 6.4481 | 4.3814 | 3.0628 | 0.4713 | 0.4713 | 0.4713 | 2.87 | 2.87 | 1.3542 | 3.3792 | 2.87 | 2.9619 | 2.9619 | 2.4759 | 4.3404 | 4.3404 | 3.2 | 3.2
Volumetric Release (actual) | m3/min | 386.8833 | 262.8833 | 183.7667 | 28.278 | 28.278 | 28.278 | 172.2015 | 172.2015 | 81.25 | 202.7534 | 172.2015 | 177.7114 | 177.7114 | 148.5541 | 260.4233 | 260.4233 | 192 | 192
Volumetric Release (actual) | m3/hr | 23213 | 15773 | 11026 | 1696.68 | 1696.68 | 1696.68 | 10332.0896 | 10332.0896 | 4875 | 12165.2043 | 10332.0896 | 10662.6828 | 10662.6828 | 8913.2463 | 15625.3968 | 15625.3968
Volumetric Release (corrected to 273K) | Nm3/s | 3.6446 | 2.5395 | 1.7169 | 0.28403 | 0.28403 | 0.28403 | 1.066 | 1.066 | 0.50298 | 1.2534 | 1.066 | 1.0986 | 1.0986 | 0.91962 | 1.61 | 1.61 | 2.25 | 2.25
Exhaust flow | kg/min | - | - | - | - | - | - | 82.6567 | 82.6567 | 39 | 97.1894 | 82.6567 | 85.1856 | 85.1856 | 71.306 | 124.8333 | 124.8333 | - | -
Exhaust flow | kg/hr | - | - | - | - | - | - | 4959.403 | 4959.403 | 2340 | 5831.3642 | 4959.403 | 5111.1338 | 5111.1338 | 4278.3582 | 7490 | 7490 | - | -
Exhaust gas density | kg/m3 | - | - | - | - | - | - | 0.48 | 0.48 | 0.48 | 0.47935 | 0.48 | 0.47935 | 0.47935 | 0.48 | 0.47935 | 0.47935 | - | -
Exhaust Gas Water Content (0 = no data) | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0
Volumetric Release (corrected to 273K, dry) | Nm3/s | 3.2801 | 2.2856 | 1.5452 | 0.25563 | 0.25563 | 0.25563 | 0.95941 | 0.95941 | 0.45268 | 1.2534 | 0.95941 | 0.98876 | 0.98876 | 0.82766 |  |  | 2.25 | 2.25
Oxygen Content in Wet Gas (5 = no data) | % | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 10 | 10
Oxygen Content in Dry Gas (5 = no data) | % | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 11.1111 | 11.1111 | 11.1111 |  |  | 5 | 5
Target O2 Content (x) | % | 3 | 3 | 3 | 3 | 3 | 3 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Volumetric Release (corrected to 273K, dry, x% O2) | Nm3/s | 2.9136 | 2.0302 | 1.3726 | 0.22706 | 0.22706 | 0.22706 | 1.7725 | 1.7725 | 0.8363 | 2.3157 | 1.7725 | 1.6405 | 1.6405 | 1.3732 | 2.9333 | 2.9333 | 6.0636 | 6.0636
Modelled NOx Emission Concentration | mg/Nm3 | 326.0564 | 280.7597 | 342.4223 | 281.4465 | 281.4465 | 281.4465 | 796.4421 | 796.4421 | 874.8807 | 1479.3291 | 796.4421 | 1830.271 | 1830.271 | 887.2245 | 1500 | 1500 | 186.3592 | 186.3592
Modelling Scenario 1 - Long-term
Combined Flues | - | Combined |  |  | Individual | Individual | Individual | - | - | - | - | - | - | - | - | - | - | Combined
Operating Hours | - | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | - | - | - | - | - | - | - | - | - | - | Continuous | Continuous
Hours Per Annum | - | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | - | - | - | - | - | - | - | - | - | - | 8760 | 8760
Modelling Scenario 2 - Short-term
Test Duration | hours | - | - | - | - | - | - | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | 1hr and 8hr | - | -
Times Per Year | - | - | - | - | - | - | - | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | 12 and 1 | - | -
Average Load Per Generator Operated | % | - | - | - | - | - | - | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | - | -
Total Hours Per Annum | hours | - | - | - | - | - | - | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | - | -
Pollutant Discharge rate from mg/Nm3
HC | g/s | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0.038928 | NA | 0.03412 | 0.03412 | NA | 0.05 | 0.05 | NA | NA
NOx | g/s | 0.95 | 0.57 | 0.47 | 0.063906 | 0.063906 | 0.063906 | 1.4117 | 1.4117 | 0.73167 | 3.4256 | 1.4117 | 3.0025 | 3.0025 | 1.2183 | 4.4 | 4.4 | 1.13 | 1.13
CO | g/s | 0.02 | 0.01 | 0.003 | NA | NA | NA | NA | NA | NA | 0.20242 | NA | 0.17742 | 0.17742 | NA | 0.26 | 0.26 | NA | NA
PM | g/s | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | NA | NA
SO2 | g/s | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0.0007007 | NA | 0.00061415 | 0.00061415 | NA | 0.0009 | 1.0009 | NA | NA
NOTES
Boiler A1, A2 and A3 emissions data taken from Table 4.1 of Report 49307000 / LERP0002 / 3009 / RH / BH, June 2010. Emission concentrations quoted as 148, 131 and 154 mg/Am3 which is likely to actually be mg/Nm3. Boilers are expected to meet ELVs of 200mg/Nm3
Emission rates for boilers A4, A5 and A6 estimated from A2, and therefore the same concentration and therefore also likely to be conservative.
Note on K7: Graham Harker: Quoted as compliant with Stage II which I believe is 6g/kWH. May be better to change to MTU rate to be conservative.
Note on K19: Graham Harker: assumed vertical velocity
Note on Q19: Graham Harker: assumed vertical velocity
Note on R19: Graham Harker: assumed vertical velocity
Note on K24: Myles Tatlock: emergency standby power (ESP) assumed
Note on Q25: Graham Harker: standby power
Note on R25: Graham Harker: standby power
Note on Q46: Graham Harker: all based on actual g/kWh
Note on R46: Graham Harker: all based on actual g/kWh
Note on K47: Graham Harker: based on g/kWh

## 2-Rcpt
Modelled Receptor Locations
Receptor ID | Name | Exposure | X (m) | Y (m) | Z (m)
CR1 | PARK ROAD | Commercial | 535021.69 | 214592.7 | 1.5
CR2 | PRIORY STREET | Commercial | 535330.31 | 214292.44 | 1.5
CR3 | WARE BOWLS CLUB | Commercial | 535414.75 | 214264.52 | 1.5
SC1 | SACRED HEART RC JMI SCHOOL | School | 535559.62 | 214133.64 | 1.5
SC2 | ST CATHERINES JMI SCHOOL | School | 534919.06 | 214614.02 | 1.5
SC3 | THE CHAUNCY SCHOOL | School | 534806 | 214661.56 | 1.5
CR4 | FANSHAWE POOL | Commercial | 534800.81 | 214583.34 | 1.5
CR5 | BROADMEADS PUMPING STATION | Commercial | 535308 | 213974 | 1.5
CR6 | GLAXOSMITHKLINE SERVICES LTD | Commercial | 535121.88 | 214367.47 | 1.5
CR7 | BROADMEADS PUMPING STATION | Commercial | 535308 | 213974 | 1.5
CR8 | ALLENBURYS SPORTS AND SOCIAL CLUB | Commercial | 534981.12 | 214376.42 | 1.5
CR9 | ELECTRICITY SUB STATION 48M FROM 86 PARK ROAD. 12M FROM UNNAMED ROAD | Commercial | 535188.5 | 214543.95 | 1.5
CR10 | STREET RECORD | Commercial | 535027.19 | 213710.23 | 1.5
CR11 | STREET RECORD | Commercial | 535321.62 | 214413.38 | 1.5
CR12 | STREET RECORD | Commercial | 535110.94 | 214477.42 | 1.5
AR1 | Cricket Ground | Amenity | 534542.06 | 214282.58 | 1.5
AR2 | Allensbury Sports Ground | Amenity | 534943.06 | 214357.58 | 1.5
AR3 | Park | Amenity | 535385.12 | 214556.22 | 1.5
AR4 | Footpath | Amenity | 534804.56 | 214239.8 | 1.5
AR5 | Footpath | Amenity | 535044.19 | 214296.52 | 1.5
AR6 | Footpath | Amenity | 534705.88 | 214368.02 | 1.5
ER1 | Lee Valey | Ecological | 537428.62 | 213290.5 | 0
ER2 | Lee Valley | Ecological | 538389.44 | 210732 | 0
ER3 | Lee Valley | Ecological | 536844.12 | 204773.66 | 0
RR1 | 4 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR2 | 6 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR3 | PRIORY STREET, WARE, SG12 9HY | Residential | 535167 | 214292 | 1.5
RR4 | 16 CHADWELL, WARE, SG12 9JY | Residential | 535312.38 | 213882.3 | 1.5
RR5 | WATTON ROAD, WARE, SG12 0HU | Residential | 535458.88 | 214569.02 | 1.5
RR6 | 2 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR7 | PARK ROAD, WARE, SG12 0DS | Residential | 534483.69 | 214428 | 1.5
RR8 | 4 CHADWELL, WARE, SG12 9JX | Residential | 535405.25 | 213931.3 | 1.5
RR9 | 3 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534645.56 | 214512 | 1.5
RR10 | 8 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR11 | 46 PRIORY STREET, WARE, SG12 0DE | Residential | 535333 | 214355 | 1.5
RR12 | 7 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR13 | 8 MYDDLETON ROAD, WARE, SG12 9JT | Residential | 535601.25 | 213994.69 | 1.5
RR14 | 56 FANSHAWE CRESCENT, WARE, SG12 0AS | Residential | 535103.75 | 214597.11 | 1.5
RR15 | MAPLETHORPE COURT, WARE, SG12 0DD | Residential | 535372.44 | 214409.62 | 1.5
RR16 | 64 PARK ROAD, WARE, SG12 0AN | Residential | 535220 | 214601.66 | 1.5
RR17 | 70 PARK ROAD, WARE, SG12 0AN | Residential | 535203 | 214599.66 | 1.5
RR18 | 15 PRIORY STREET, WARE, SG12 0DE | Residential | 535365.88 | 214341.17 | 1.5
RR19 | 29 CHADWELL, WARE, SG12 9JY | Residential | 535189.19 | 213782.27 | 1.5
RR20 | 24 CHADWELL, WARE, SG12 9JY | Residential | 535215 | 213810.02 | 1.5
RR21 | MAPLETHORPE COURT, WARE, SG12 0DD | Residential | 535384.19 | 214421 | 1.5
RR22 | PARK ROAD, WARE, SG12 0DS | Residential | 534482 | 214427 | 1.5
RR23 | 34 BROADMEADS, WARE, SG12 9HU | Residential | 535670 | 214169 | 1.5
RR24 | 15 COWPER CLOSE, WARE, SG12 0GG | Residential | 534763.94 | 214555.36 | 1.5
RR25 | 10 COWPER CLOSE, WARE, SG12 0GG | Residential | 534716.31 | 214558.59 | 1.5
RR26 | 1 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR27 | 5 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR28 | 418 WARE ROAD, HERTFORD, SG13 7EW | Residential | 534796 | 213533.06 | 1.5
RR29 | 10 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR30 | 12 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR31 | 9 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR32 | 21 CHADWELL, WARE, SG12 9JY | Residential | 535256.69 | 213835.3 | 1.5
RR33 | 16 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR34 | 1 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR35 | 15 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR36 | 14 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR37 | 3 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR38 | HERTFORD ROAD, WARE, SG12 9AX | Residential | 535124.25 | 213698.91 | 1.5
RR39 | 3 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR40 | 6 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR41 | 90 PARK ROAD, WARE, SG12 0AN | Residential | 535130.62 | 214595.33 | 1.5
RR42 | 1 CHADWELL, WARE, SG12 9JX | Residential | 535424.62 | 213945.08 | 1.5
RR43 | 8 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR44 | 2 BROADMEADS, WARE, SG12 9HT | Residential | 535641 | 214086 | 1.5
RR45 | 14 CHADWELL, WARE, SG12 9JY | Residential | 535324.38 | 213889.3 | 1.5
RR46 | 4 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR47 | 5 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR48 | 7 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR49 | 5 BURYFIELD TERRACE, WARE, SG12 0DF | Residential | 535327 | 214389 | 1.5
RR50 | 13 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR51 | 11 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR52 | 17 WATTON ROAD, WARE, SG12 0HU | Residential | 535457.69 | 214536.09 | 1.5
RR53 | 27 CHADWELL, WARE, SG12 9JY | Residential | 535200.06 | 213795.27 | 1.5
RR54 | MAPLETHORPE COURT, WARE, SG12 0DD | Residential | 535375 | 214402 | 1.5
RR55 | 6 HILLSIDE, WARE, SG12 9JZ | Residential | 535541.12 | 213986.23 | 1.5
RR56 | 17 CHADWELL, WARE, SG12 9JY | Residential | 535300.38 | 213874.3 | 1.5
RR57 | 8 HILLSIDE, WARE, SG12 9JZ | Residential | 535524.31 | 213984.5 | 1.5
RR58 | MAPLETHORPE COURT, WARE, SG12 0DD | Residential | 535384.19 | 214421 | 1.5
RR59 | 1 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535518.12 | 214441.09 | 1.5
RR60 | 18 COWPER CLOSE, WARE, SG12 0GG | Residential | 534782.88 | 214562.19 | 1.5
RR61 | 36 BROADMEADS, WARE, SG12 9HU | Residential | 535670 | 214169 | 1.5
RR62 | 31 BROADMEADS, WARE, SG12 9HU | Residential | 535670 | 214169 | 1.5
RR63 | 17 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR64 | 14 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR65 | 15 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR66 | 20 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR67 | 28 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR68 | 11 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR69 | 29 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR70 | 10 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR71 | 25 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR72 | 25 HILLSIDE, WARE, SG12 9JZ | Residential | 535456.12 | 213961.72 | 1.5
RR73 | 9 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR74 | 17 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR75 | 27 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR76 | 22 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR77 | 19 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR78 | 16 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR79 | 13 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR80 | 15 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR81 | 12 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR82 | 26 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR83 | 19 CHADWELL, WARE, SG12 9JY | Residential | 535278.69 | 213854.3 | 1.5
RR84 | 54 PARK ROAD, WARE, SG12 0AN | Residential | 535253.38 | 214598.72 | 1.5
RR85 | 12 COWPER CLOSE, WARE, SG12 0GG | Residential | 534733.88 | 214552.03 | 1.5
RR86 | 1 BURYFIELD TERRACE, WARE, SG12 0DF | Residential | 535330 | 214374 | 1.5
RR87 | 16 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR88 | 30 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR89 | 21 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR90 | 79 FANSHAWE CRESCENT, WARE, SG12 0AR | Residential | 535072.25 | 214596.33 | 1.5
RR91 | 1 MYDDLETON ROAD, WARE, SG12 9JT | Residential | 535642.12 | 213990.97 | 1.5
RR92 | 4 HILLSIDE, WARE, SG12 9JZ | Residential | 535557.12 | 213989.23 | 1.5
RR93 | 1 HILLSIDE, WARE, SG12 9JZ | Residential | 535578.12 | 213989.23 | 1.5
RR94 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR95 | WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR96 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR97 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR98 | 24 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR99 | 14 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR100 | 10 CHADWELL, WARE, SG12 9JX | Residential | 535359.56 | 213908.88 | 1.5
RR101 | 18 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR102 | 8 CHADWELL, WARE, SG12 9JX | Residential | 535370.75 | 213913.81 | 1.5
RR103 | 12 BLACK SWAN COURT, WARE, SG12 0HY | Residential | 535520.38 | 214477.55 | 1.5
RR104 | 23 BROADMEADS, WARE, SG12 9HT | Residential | 535648 | 214142 | 1.5
RR105 | 13 BROADMEADS, WARE, SG12 9HT | Residential | 535639 | 214110 | 1.5
RR106 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR107 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR108 | 399 WARE ROAD, HERTFORD, SG13 7EN | Residential | 534708 | 213515.94 | 1.5
RR109 | 47 PARK ROAD, WARE, SG12 0AJ | Residential | 535322 | 214570 | 1.5
RR110 | 84 PARK ROAD, WARE, SG12 0AN | Residential | 535159 | 214598.66 | 1.5
RR111 | 6 CHADWELL, WARE, SG12 9JX | Residential | 535387.5 | 213925.69 | 1.5
RR112 | 5 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534599 | 214496 | 1.5
RR113 | PARK ROAD, WARE, SG12 0DS | Residential | 534453.69 | 214398.55 | 1.5
RR114 | 49 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534538.88 | 214467.92 | 1.5
RR115 | 57 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534516.25 | 214460.61 | 1.5
RR116 | 6 THE BRICKFIELDS, WARE, SG12 0AZ | Residential | 534686.5 | 214539.06 | 1.5
RR117 | 41 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534559.56 | 214479.97 | 1.5
RR118 | 33 TRAPSTYLE ROAD, WARE, SG12 0BA | Residential | 534579.62 | 214493.19 | 1.5
RR119 | 31 CHADWELL, WARE, SG12 9LD | Residential | 535173.69 | 213760.16 | 1.5
RR120 | HERTFORD ROAD, WARE, SG12 9LF | Residential | 535071.94 | 213690.45 | 1.5
RR121 | 6 BURGAGE LANE, WARE, SG12 9XD | Residential | 535659 | 214261 | 1.5
RR122 | 12 BURGAGE LANE, WARE, SG12 9XD | Residential | 535677 | 214232 | 1.5
RR123 | 76 PARK ROAD, WARE, SG12 0AN | Residential | 535184 | 214599.66 | 1.5
RR124 | 58 PARK ROAD, WARE, SG12 0AN | Residential | 535239 | 214601.66 | 1.5
RR125 | 104 PARK ROAD, WARE, SG12 0AW | Residential | 535033.5 | 214591.97 | 1.5
RR126 | 10 HILLSIDE, WARE, SG12 9JZ | Residential | 535507.31 | 213975.5 | 1.5
RR127 | 36 CHADWELL, WARE, SG12 9LD | Residential | 535146.44 | 213724.45 | 1.5
RR128 | 12 CHADWELL, WARE, SG12 9JY | Residential | 535339.06 | 213898.95 | 1.5
ER1 | Lee Valley | SSSI/RAMSAR/SAC | 537428.62 | 213290.5 | 0
ER2 | Lee Valley | SSSI/RAMSAR/SAC | 538389.44 | 210732 | 0
ER3 | Lee Valley | SSSI/RAMSAR/SAC | 536844.12 | 204773.66 | 0
ER4 | Wormley-Hoddesdonpark Woods North | SSSI/SAC | 535207.75 | 208992.55 | 0
ER5 | Wormley-Hoddesdonpark Woods North | SSSI/SAC | 532430.31 | 207691 | 0
ER6 | Wormley-Hoddesdonpark Woods South | SSSI/SAC | 532011.44 | 206625.62 | 0
LWS1 | Tumbling Bay Gravel Pit | LWS | 536412.12 | 214101.48 | 0
LWS2 | Post Wood Road Area | LWS | 536048.38 | 213873.66 | 0
LWS3 | Post Wood | LWS | 536012.38 | 213350.44 | 0
LWS4 | Ware Lines Quarry | LWS | 534701.69 | 213374.95 | 0
LWS5 | Ware Park Monastery | LWS | 534068 | 214494 | 0
LWS6 | Meadow E. Of New River, Ware | LWS | 536177 | 213761.58 | 0
LWS7 | Ware Chalk Mine | LWS | 535169 | 213657 | 0
LWS8 | Scotts Grotto (Ware) | LWS | 535673 | 213828 | 0
LWS9 | Kings Mead | LWS | 534789.56 | 214231.94 | 0
LWS10 | R. Beane, R. Lea & Lower R. Rib Confluence | LWS | 533562.88 | 213867.77 | 0
LWS11 | Kings Mead | LWS | 534375.19 | 214135 | 0

## 3-Rslts LT NO2
Results - Annual Mean NO2
NO2
[6 empty] | 18.6005 | Thermal Plant CHP | Thermal Plant Boilers | Thermal Plant Total | Gen Sets | All Plant
| Exposure | Receptor name | X(m) | Y(m) | Z(m) | BG | AM NO2 PC | AM NO2 PC | AM NO2 PC | AM NO2 PC after Adjust | AM NO2 PC | PC as a % of AQO | PEC NO2 | PEC as a % of AQO
| CR | CR1 | 535021.69 | 214592.7 | 1.5 | 18.6005 | 2.7487 | 1.8611 | 4.6099 | 0.58372 | 5.1936 | 12.9839 | 23.7941 | 59.4852
| CR | CR2 | 535330.31 | 214292.44 | 1.5 | 18.6005 | 1.1392 | 0.78996 | 1.9292 | 0.045394 | 1.9746 | 4.9365 | 20.5751 | 51.4377
| CR | CR3 | 535414.75 | 214264.52 | 1.5 | 18.6005 | 0.89728 | 0.66801 | 1.5653 | 0.035315 | 1.6006 | 4.0015 | 20.2011 | 50.5028
| SC | SC1 | 535559.62 | 214133.64 | 1.5 | 18.6005 | 0.60572 | 0.45902 | 1.0647 | 0.022506 | 1.0872 | 2.7181 | 19.6877 | 49.2194
| SC | SC2 | 534919.06 | 214614.02 | 1.5 | 14.8347 | 3.0843 | 1.7436 | 4.8279 | 0.41237 | 5.2402 | 13.1006 | 20.0749 | 50.1873
| SC | SC3 | 534806 | 214661.56 | 1.5 | 14.8347 | 2.0999 | 0.84382 | 2.9381 | 0.29968 | 3.2377 | 8.0943 | 18.0724 | 45.181
| CR | CR4 | 534800.81 | 214583.34 | 1.5 | 14.8347 | 2.469 | 0.60126 | 3.0702 | 0.5476 | 3.6178 | 9.0446 | 18.4525 | 46.1313
| CR | CR5 | 535308 | 213974 | 1.5 | 13.5292 | 0.70559 | 0.4456 | 1.1512 | 0.027544 | 1.1787 | 2.9468 | 14.708 | 36.7699
| CR | CR6 | 535121.88 | 214367.47 | 1.5 | 18.6005 | 2.7526 | 1.2249 | 3.9775 | 0.10895 | 4.0865 | 10.2162 | 22.687 | 56.7174
| CR | CR7 | 535308 | 213974 | 1.5 | 13.5292 | 0.70559 | 0.4456 | 1.1512 | 0.027544 | 1.1787 | 2.9468 | 14.708 | 36.7699
| CR | CR8 | 534981.12 | 214376.42 | 1.5 | 14.8347 | 5.1795 | 1.7251 | 6.9046 | 0.21114 | 7.1157 | 17.7893 | 21.9504 | 54.876
| CR | CR9 | 535188.5 | 214543.95 | 1.5 | 18.6005 | 2.2808 | 1.5247 | 3.8055 | 0.12295 | 3.9285 | 9.8212 | 22.529 | 56.3224
| CR | CR10 | 535027.19 | 213710.23 | 1.5 | 13.5292 | 0.40462 | 0.25005 | 0.6458 | 0.020415 | 0.66621 | 1.6655 | 14.1954 | 35.4886
| CR | CR11 | 535321.62 | 214413.38 | 1.5 | 18.6005 | 1.4024 | 0.9402 | 2.3426 | 0.058085 | 2.4007 | 6.0018 | 21.0012 | 52.503
| CR | CR12 | 535110.94 | 214477.42 | 1.5 | 18.6005 | 3.1566 | 1.6149 | 4.7716 | 0.18365 | 4.9552 | 12.3881 | 23.5557 | 58.8893
| AR | AR1 | 534542.06 | 214282.58 | 1.5 | 14.8347 | 1.3656 | 0.44795 | 1.7494 | 0.073247 | 1.8226 | 4.5565 | 16.6573 | 41.6432
| AR | AR2 | 534943.06 | 214357.58 | 1.5 | 14.8347 | 5.2285 | 1.3635 | 6.592 | 0.29572 | 6.8878 | 17.2194 | 21.7224 | 54.3061
| AR | AR3 | 535385.12 | 214556.22 | 1.5 | 18.6005 | 1.3346 | 0.98204 | 2.3167 | 0.055206 | 2.3719 | 5.9297 | 20.9724 | 52.4309
| AR | AR4 | 534804.56 | 214239.8 | 1.5 | 14.8347 | 4.139 | 0.84156 | 4.6601 | 0.14872 | 4.8088 | 12.022 | 19.6435 | 49.1087
| AR | AR5 | 535044.19 | 214296.52 | 1.5 | 18.6005 | 2.8459 | 1.0552 | 3.9011 | 0.11984 | 4.0209 | 10.0524 | 22.6214 | 56.5536
| AR | AR6 | 534705.88 | 214368.02 | 1.5 | 14.8347 | 0.32779 | 0.29998 | 0.62479 | 1.002 | 1.6268 | 4.0669 | 16.4614 | 41.1536
| RR | RR1 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR2 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR3 | 535167 | 214292 | 1.5 | 18.6005 | 1.8418 | 0.98324 | 2.8251 | 0.074319 | 2.8994 | 7.2485 | 21.4999 | 53.7497
| RR | RR4 | 535312.38 | 213882.3 | 1.5 | 13.5292 | 0.60492 | 0.37459 | 0.97951 | 0.022972 | 1.0025 | 2.5062 | 14.5317 | 36.3293
| RR | RR5 | 535458.88 | 214569.02 | 1.5 | 18.6005 | 1.116 | 0.84861 | 1.9646 | 0.04459 | 2.0092 | 5.0231 | 20.6097 | 51.5243
| RR | RR6 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR7 | 534483.69 | 214428 | 1.5 | 14.8347 | 1.1231 | 0.38599 | 1.4348 | 0.074513 | 1.5093 | 3.7732 | 16.344 | 40.8599
| RR | RR8 | 535405.25 | 213931.3 | 1.5 | 13.5292 | 0.57883 | 0.38693 | 0.96576 | 0.022353 | 0.98812 | 2.4703 | 14.5173 | 36.2934
| RR | RR9 | 534645.56 | 214512 | 1.5 | 14.8347 | 1.8195 | 0.45358 | 2.273 | 0.26897 | 2.542 | 6.3551 | 17.3767 | 43.4418
| RR | RR10 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR11 | 535333 | 214355 | 1.5 | 18.6005 | 1.2306 | 0.85899 | 2.0896 | 0.050272 | 2.1399 | 5.3497 | 20.7404 | 51.8509
| RR | RR12 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR13 | 535601.25 | 213994.69 | 1.5 | 13.5292 | 0.50229 | 0.35932 | 0.86161 | 0.017787 | 0.8794 | 2.1985 | 14.4086 | 36.0216
| RR | RR14 | 535103.75 | 214597.11 | 1.5 | 18.6005 | 2.4141 | 1.7131 | 4.1056 | 0.20777 | 4.3134 | 10.7835 | 22.9139 | 57.2848
| RR | RR15 | 535372.44 | 214409.62 | 1.5 | 18.6005 | 1.1974 | 0.84807 | 2.0455 | 0.049175 | 2.0947 | 5.2367 | 20.6952 | 51.7379
| RR | RR16 | 535220 | 214601.66 | 1.5 | 18.6005 | 1.8734 | 1.4457 | 3.3191 | 0.10409 | 3.4231 | 8.5579 | 22.0236 | 55.0591
| RR | RR17 | 535203 | 214599.66 | 1.5 | 18.6005 | 1.9471 | 1.4937 | 3.4408 | 0.11279 | 3.5536 | 8.8839 | 22.1541 | 55.3852
| RR | RR18 | 535365.88 | 214341.17 | 1.5 | 18.6005 | 1.1014 | 0.79761 | 1.899 | 0.044769 | 1.9438 | 4.8594 | 20.5443 | 51.3607
| RR | RR19 | 535189.19 | 213782.27 | 1.5 | 13.5292 | 0.51201 | 0.31046 | 0.82247 | 0.020797 | 0.84327 | 2.1082 | 14.3725 | 35.9312
| RR | RR20 | 535215 | 213810.02 | 1.5 | 13.5292 | 0.54765 | 0.32969 | 0.87734 | 0.021487 | 0.89883 | 2.2471 | 14.4281 | 36.0701
| RR | RR21 | 535384.19 | 214421 | 1.5 | 18.6005 | 1.1786 | 0.83903 | 2.0176 | 0.048243 | 2.0659 | 5.1647 | 20.6664 | 51.6659
| RR | RR22 | 534482 | 214427 | 1.5 | 14.8347 | 1.1165 | 0.38443 | 1.4272 | 0.073823 | 1.501 | 3.7526 | 16.3357 | 40.8393
| RR | RR23 | 535670 | 214169 | 1.5 | 18.6005 | 0.52096 | 0.42476 | 0.94572 | 0.019537 | 0.96526 | 2.4131 | 19.5658 | 48.9144
| RR | RR24 | 534763.94 | 214555.36 | 1.5 | 14.8347 | 2.2217 | 0.51516 | 2.7331 | 0.56169 | 3.2948 | 8.2371 | 18.1295 | 45.3238
| RR | RR25 | 534716.31 | 214558.59 | 1.5 | 14.8347 | 2.1594 | 0.49836 | 2.6578 | 0.41873 | 3.0765 | 7.6912 | 17.9112 | 44.7779
| RR | RR26 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR27 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR28 | 534796 | 213533.06 | 1.5 | 14.5392 | 0.33906 | 0.23056 | 0.56962 | 0.017595 | 0.58722 | 1.468 | 15.1264 | 37.8161
| RR | RR29 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR30 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR31 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR32 | 535256.69 | 213835.3 | 1.5 | 13.5292 | 0.57325 | 0.34649 | 0.91974 | 0.021844 | 0.94159 | 2.354 | 14.4708 | 36.177
| RR | RR33 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR34 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR35 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR36 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR37 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR38 | 535124.25 | 213698.91 | 1.5 | 13.5292 | 0.40981 | 0.25353 | 0.66334 | 0.018368 | 0.68171 | 1.7043 | 14.2109 | 35.5273
| RR | RR39 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR40 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR41 | 535130.62 | 214595.33 | 1.5 | 18.6005 | 2.2815 | 1.6753 | 3.9568 | 0.17093 | 4.1277 | 10.3192 | 22.7282 | 56.8205
| RR | RR42 | 535424.62 | 213945.08 | 1.5 | 13.5292 | 0.57722 | 0.38947 | 0.96669 | 0.022128 | 0.98882 | 2.4721 | 14.5181 | 36.2951
| RR | RR43 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR44 | 535641 | 214086 | 1.5 | 18.6005 | 0.51678 | 0.39466 | 0.91143 | 0.018713 | 0.93015 | 2.3254 | 19.5306 | 48.8266
| RR | RR45 | 535324.38 | 213889.3 | 1.5 | 13.5292 | 0.60372 | 0.3777 | 0.98143 | 0.022985 | 1.0044 | 2.511 | 14.5336 | 36.3341
| RR | RR46 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR47 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR48 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR49 | 535327 | 214389 | 1.5 | 18.6005 | 1.3235 | 0.90432 | 2.2278 | 0.054571 | 2.2824 | 5.706 | 20.8829 | 52.2072
| RR | RR50 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR51 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR52 | 535457.69 | 214536.09 | 1.5 | 18.6005 | 1.1035 | 0.82283 | 1.9264 | 0.043663 | 1.97 | 4.925 | 20.5705 | 51.4263
| RR | RR53 | 535200.06 | 213795.27 | 1.5 | 13.5292 | 0.52878 | 0.31946 | 0.84824 | 0.021183 | 0.86942 | 2.1736 | 14.3987 | 35.9966
| RR | RR54 | 535375 | 214402 | 1.5 | 18.6005 | 1.1746 | 0.83721 | 2.0118 | 0.048228 | 2.06 | 5.15 | 20.6605 | 51.6512
| RR | RR55 | 535541.12 | 213986.23 | 1.5 | 13.5292 | 0.53463 | 0.37422 | 0.90885 | 0.019157 | 0.92801 | 2.32 | 14.4572 | 36.1431
| RR | RR56 | 535300.38 | 213874.3 | 1.5 | 13.5292 | 0.60336 | 0.37046 | 0.97382 | 0.022897 | 0.99672 | 2.4918 | 14.5259 | 36.3149
| RR | RR57 | 535524.31 | 213984.5 | 1.5 | 13.5292 | 0.54422 | 0.37888 | 0.9231 | 0.019644 | 0.94274 | 2.3569 | 14.472 | 36.1799
| RR | RR58 | 535384.19 | 214421 | 1.5 | 18.6005 | 1.1786 | 0.83903 | 2.0176 | 0.048243 | 2.0659 | 5.1647 | 20.6664 | 51.6659
| RR | RR59 | 535518.12 | 214441.09 | 1.5 | 18.6005 | 0.86218 | 0.66442 | 1.5266 | 0.03427 | 1.5609 | 3.9022 | 20.1614 | 50.4034
| RR | RR60 | 534782.88 | 214562.19 | 1.5 | 14.8347 | 2.2942 | 0.54575 | 2.8399 | 0.66729 | 3.5072 | 8.768 | 18.3419 | 45.8547
| RR | RR61 | 535670 | 214169 | 1.5 | 18.6005 | 0.52096 | 0.42476 | 0.94572 | 0.019537 | 0.96526 | 2.4131 | 19.5658 | 48.9144
| RR | RR62 | 535670 | 214169 | 1.5 | 18.6005 | 0.52096 | 0.42476 | 0.94572 | 0.019537 | 0.96526 | 2.4131 | 19.5658 | 48.9144
| RR | RR63 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR64 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR65 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR66 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR67 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR68 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR69 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR70 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR71 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR72 | 535456.12 | 213961.72 | 1.5 | 13.5292 | 0.57036 | 0.38896 | 0.95932 | 0.021474 | 0.9808 | 2.452 | 14.51 | 36.2751
| RR | RR73 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR74 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR75 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR76 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR77 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR78 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR79 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR80 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR81 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR82 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR83 | 535278.69 | 213854.3 | 1.5 | 13.5292 | 0.59011 | 0.35844 | 0.94855 | 0.022442 | 0.97099 | 2.4275 | 14.5002 | 36.2506
| RR | RR84 | 535253.38 | 214598.72 | 1.5 | 18.6005 | 1.762 | 1.3545 | 3.1164 | 0.090124 | 3.2066 | 8.0164 | 21.8071 | 54.5176
| RR | RR85 | 534733.88 | 214552.03 | 1.5 | 14.8347 | 2.1515 | 0.47937 | 2.6308 | 0.58799 | 3.2188 | 8.0471 | 18.0535 | 45.1338
| RR | RR86 | 535330 | 214374 | 1.5 | 18.6005 | 1.2794 | 0.88368 | 2.163 | 0.052561 | 2.2156 | 5.539 | 20.8161 | 52.0403
| RR | RR87 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR88 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR89 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR90 | 535072.25 | 214596.33 | 1.5 | 18.6005 | 2.6228 | 1.7489 | 4.2993 | 0.28126 | 4.5806 | 11.4515 | 23.1811 | 57.9527
| RR | RR91 | 535642.12 | 213990.97 | 1.5 | 13.5292 | 0.47601 | 0.34519 | 0.8212 | 0.016748 | 0.83795 | 2.0949 | 14.3672 | 35.9179
| RR | RR92 | 535557.12 | 213989.23 | 1.5 | 13.5292 | 0.52645 | 0.37057 | 0.89702 | 0.018798 | 0.91582 | 2.2895 | 14.445 | 36.1126
| RR | RR93 | 535578.12 | 213989.23 | 1.5 | 13.5292 | 0.51329 | 0.36382 | 0.87711 | 0.018255 | 0.89536 | 2.2384 | 14.4246 | 36.0615
| RR | RR94 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR95 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR96 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR97 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR98 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR99 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR100 | 535359.56 | 213908.88 | 1.5 | 13.5292 | 0.59418 | 0.38431 | 0.97849 | 0.0229 | 1.0014 | 2.5035 | 14.5306 | 36.3265
| RR | RR101 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR102 | 535370.75 | 213913.81 | 1.5 | 13.5292 | 0.58951 | 0.38497 | 0.97448 | 0.022784 | 0.99726 | 2.4932 | 14.5265 | 36.3162
| RR | RR103 | 535520.38 | 214477.55 | 1.5 | 18.6005 | 0.89649 | 0.68459 | 1.5811 | 0.035193 | 1.6163 | 4.0407 | 20.2168 | 50.5419
| RR | RR104 | 535648 | 214142 | 1.5 | 18.6005 | 0.53052 | 0.42197 | 0.95249 | 0.01968 | 0.97217 | 2.4304 | 19.5727 | 48.9317
| RR | RR105 | 535639 | 214110 | 1.5 | 18.6005 | 0.52682 | 0.40866 | 0.93547 | 0.019277 | 0.95475 | 2.3869 | 19.5553 | 48.8881
| RR | RR106 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR107 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR108 | 534708 | 213515.94 | 1.5 | 14.5392 | 0.35783 | 0.24004 | 0.59787 | 0.017859 | 0.61573 | 1.5393 | 15.155 | 37.8874
| RR | RR109 | 535322 | 214570 | 1.5 | 18.6005 | 1.561 | 1.1485 | 2.7096 | 0.068907 | 2.7785 | 6.9462 | 21.379 | 53.4475
| RR | RR110 | 535159 | 214598.66 | 1.5 | 18.6005 | 2.1319 | 1.6075 | 3.7394 | 0.14244 | 3.8818 | 9.7045 | 22.4823 | 56.2057
| RR | RR111 | 535387.5 | 213925.69 | 1.5 | 13.5292 | 0.58695 | 0.38836 | 0.97531 | 0.022726 | 0.99804 | 2.4951 | 14.5273 | 36.3182
| RR | RR112 | 534599 | 214496 | 1.5 | 14.8347 | 1.4222 | 0.45883 | 1.8811 | 0.17382 | 2.0549 | 5.1372 | 16.8896 | 42.2239
| RR | RR113 | 534453.69 | 214398.55 | 1.5 | 14.8347 | 0.95548 | 0.34899 | 1.25 | 0.061239 | 1.3112 | 3.2781 | 16.1459 | 40.3648
| RR | RR114 | 534538.88 | 214467.92 | 1.5 | 14.8347 | 1.2061 | 0.42897 | 1.5602 | 0.10778 | 1.6679 | 4.1699 | 16.5026 | 41.2566
| RR | RR115 | 534516.25 | 214460.61 | 1.5 | 14.8347 | 1.1905 | 0.41989 | 1.5297 | 0.09446 | 1.6241 | 4.0604 | 16.4588 | 41.1471
| RR | RR116 | 534686.5 | 214539.06 | 1.5 | 14.8347 | 2.2016 | 0.47498 | 2.6708 | 0.35692 | 3.0277 | 7.5693 | 17.8624 | 44.656
| RR | RR117 | 534559.56 | 214479.97 | 1.5 | 14.8347 | 1.1968 | 0.44364 | 1.6404 | 0.12585 | 1.7663 | 4.4157 | 16.601 | 41.5024
| RR | RR118 | 534579.62 | 214493.19 | 1.5 | 14.8347 | 1.3021 | 0.45947 | 1.7616 | 0.14861 | 1.9102 | 4.7756 | 16.7449 | 41.8623
| RR | RR119 | 535173.69 | 213760.16 | 1.5 | 13.5292 | 0.48364 | 0.29543 | 0.77907 | 0.02013 | 0.7992 | 1.998 | 14.3284 | 35.8211
| RR | RR120 | 535071.94 | 213690.45 | 1.5 | 13.5292 | 0.39326 | 0.24062 | 0.63063 | 0.018625 | 0.64926 | 1.6231 | 14.1785 | 35.4462
| RR | RR121 | 535659 | 214261 | 1.5 | 18.6005 | 0.55348 | 0.46767 | 1.0212 | 0.021717 | 1.0429 | 2.6072 | 19.6434 | 49.1084
| RR | RR122 | 535677 | 214232 | 1.5 | 18.6005 | 0.52973 | 0.44659 | 0.97632 | 0.020519 | 0.99684 | 2.4921 | 19.5973 | 48.9933
| RR | RR123 | 535184 | 214599.66 | 1.5 | 18.6005 | 2.0223 | 1.544 | 3.5664 | 0.12408 | 3.6905 | 9.2261 | 22.291 | 55.7274
| RR | RR124 | 535239 | 214601.66 | 1.5 | 18.6005 | 1.8031 | 1.3934 | 3.1965 | 0.095671 | 3.2922 | 8.2305 | 21.8927 | 54.7317
| RR | RR125 | 535033.5 | 214591.97 | 1.5 | 18.6005 | 2.7498 | 1.8179 | 4.5678 | 0.49369 | 5.0614 | 12.6536 | 23.6619 | 59.1549
| RR | RR126 | 535507.31 | 213975.5 | 1.5 | 13.5292 | 0.54824 | 0.37965 | 0.92789 | 0.020048 | 0.94794 | 2.3699 | 14.4772 | 36.1929
| RR | RR127 | 535146.44 | 213724.45 | 1.5 | 13.5292 | 0.43993 | 0.27117 | 0.7111 | 0.019078 | 0.73018 | 1.8254 | 14.2594 | 35.6485
| RR | RR128 | 535339.06 | 213898.95 | 1.5 | 13.5292 | 0.60176 | 0.38182 | 0.98358 | 0.023025 | 1.0066 | 2.5165 | 14.5358 | 36.3396
Note on K3: Ben Madge: nox to NO2 conversion factor

## 4-Rslts ST NO2
[5 empty] | NO2 | Generator Plant (Continuous)
[5 empty] | 18.6005 | 2014 | 2015 | 2016 | 2017 | 2018 | [13 empty] | Thermal Plant CHP | Thermal Plant Boilers | Thermal Plant Total
Exposure | Receptor name | X(m) | Y(m) | Z(m) | BG | EXpaM¦NOx¦ 0.43787E+03 ug/m3¦<All sources>¦-¦ 1hr | EXpaM¦NOx¦ 0.43787E+03 ug/m3¦<All sources>¦-¦ 1hr | EXpaM¦NOx¦ 0.43787E+03 ug/m3¦<All sources>¦-¦ 1hr | EXpaM¦NOx¦ 0.43787E+03 ug/m3¦<All sources>¦-¦ 1hr | EXpaM¦NOx¦ 0.43787E+03 ug/m3¦<All sources>¦-¦ 1hr | HM Max Number Exceedances | Successes in sample | Sample size | Successes in pop | Population | CumHypGeoDist | Probability (%) | Exposure | Receptor name | X(m) | Y(m) | Z(m) | BG | P99 NO2 PC | P99 NO2 PC | P99 NO2 PC | PC as a % of AQO | PEC NO2 | PEC as a % of AQO
CR | CR1 | 535021.69 | 214592.7 | 1.5 | 37.2 | 2139.5 | 2442.38 | 2175.95 | 2447.35 | 1911.51 | 2447.35 | 2 | 20 | 6312.65 | 8760 | 1.065e-08 | 1.065e-06 | CR | CR1 | 535021.69 | 214592.7 | 1.5 | 37.201 | 15.6192 | 9.8427 | 19.0183 | 9.5092 | 56.2193 | 28.1097
CR | CR2 | 535330.31 | 214292.44 | 1.5 | 37.2 | 38.1318 | 31.5474 | 43.9277 | 24.2212 | 32.1431 | 43.9277 | 2 | 20 | 8716.0723 | 8761 | 2.2838e-41 | 2.2838e-39 | CR | CR2 | 535330.31 | 214292.44 | 1.5 | 37.201 | 1.1392 | 0.78996 | 1.9292 | 0.9646 | 39.1302 | 19.5651
CR | CR3 | 535414.75 | 214264.52 | 1.5 | 37.2 | 37.1012 | 29.5121 | 37.7983 | 20.1843 | 27.1207 | 37.7983 | 2 | 20 | 8722.2017 | 8762 | 1.5076e-42 | 1.5076e-40 | CR | CR3 | 535414.75 | 214264.52 | 1.5 | 37.201 | 0.89728 | 0.66801 | 1.5653 | 0.78265 | 38.7663 | 19.3831
SC | SC1 | 535559.62 | 214133.64 | 1.5 | 37.2 | 32.9788 | 24.4238 | 25.5394 | 16.1475 | 23.1029 | 32.9788 | 2 | 20 | 8727.0212 | 8763 | 1.2053e-43 | 1.2053e-41 | SC | SC1 | 535559.62 | 214133.64 | 1.5 | 37.201 | 0.60572 | 0.45902 | 1.0647 | 0.53237 | 38.2657 | 19.1329
SC | SC2 | 534919.06 | 214614.02 | 1.5 | 37.2 | 1445.92 | 1688.29 | 1405.69 | 1605.66 | 1259.61 | 1688.29 | 2 | 20 | 7071.71 | 8764 | 1.6607e-11 | 1.6607e-09 | SC | SC2 | 534919.06 | 214614.02 | 1.5 | 29.6694 | 3.0843 | 1.7436 | 4.8279 | 2.4139 | 34.4972 | 17.2486
SC | SC3 | 534806 | 214661.56 | 1.5 | 37.2 | 1295.45 | 946.422 | 1213.63 | 1087.94 | 1231.48 | 1295.45 | 2 | 20 | 7464.55 | 8765 | 1.558e-13 | 1.558e-11 | SC | SC3 | 534806 | 214661.56 | 1.5 | 29.6694 | 2.0999 | 0.84382 | 2.9381 | 1.469 | 32.6074 | 16.3037
CR | CR4 | 534800.81 | 214583.34 | 1.5 | 37.2 | 1761.28 | 1327.03 | 1601.83 | 1470.43 | 1720.66 | 1761.28 | 2 | 20 | 6998.72 | 8766 | 3.5516e-11 | 3.5516e-09 | CR | CR4 | 534800.81 | 214583.34 | 1.5 | 29.6694 | 2.469 | 0.60126 | 3.0702 | 1.5351 | 32.7396 | 16.3698
CR | CR5 | 535308 | 213974 | 1.5 | 37.2 | 39.1624 | 42.7416 | 42.9061 | 30.2765 | 31.1386 | 42.9061 | 2 | 20 | 8717.0939 | 8767 | 2.3709e-40 | 2.3709e-38 | CR | CR5 | 535308 | 213974 | 1.5 | 27.0585 | 0.70559 | 0.4456 | 1.1512 | 0.57559 | 28.2096 | 14.1048
CR | CR6 | 535121.88 | 214367.47 | 1.5 | 37.2 | 100.998 | 73.2714 | 106.244 | 78.7189 | 77.3443 | 106.244 | 2 | 20 | 8653.756 | 8768 | 6.137e-33 | 6.137e-31 | CR | CR6 | 535121.88 | 214367.47 | 1.5 | 37.201 | 2.7526 | 1.2249 | 3.9775 | 1.9888 | 41.1785 | 20.5893
CR | CR7 | 535308 | 213974 | 1.5 | 37.2 | 39.1624 | 42.7416 | 42.9061 | 30.2765 | 31.1386 | 42.9061 | 2 | 20 | 8717.0939 | 8769 | 5.5785e-40 | 5.5785e-38 | CR | CR7 | 535308 | 213974 | 1.5 | 27.0585 | 0.70559 | 0.4456 | 1.1512 | 0.57559 | 28.2096 | 14.1048
CR | CR8 | 534981.12 | 214376.42 | 1.5 | 37.2 | 498.805 | 519.006 | 588.427 | 687.276 | 519.312 | 687.276 | 2 | 20 | 8072.724 | 8770 | 2.1844e-18 | 2.1844e-16 | CR | CR8 | 534981.12 | 214376.42 | 1.5 | 29.6694 | 5.1795 | 1.7251 | 6.9046 | 3.4523 | 36.5739 | 18.287
CR | CR9 | 535188.5 | 214543.95 | 1.5 | 37.2 | 183.445 | 138.401 | 219.638 | 201.843 | 156.698 | 219.638 | 2 | 20 | 8540.362 | 8771 | 3.4754e-27 | 3.4754e-25 | CR | CR9 | 535188.5 | 214543.95 | 1.5 | 37.201 | 2.2808 | 1.5247 | 3.8055 | 1.9028 | 41.0065 | 20.5033
CR | CR10 | 535027.19 | 213710.23 | 1.5 | 37.2 | 48.4376 | 40.7063 | 36.7767 | 19.1751 | 27.1207 | 48.4376 | 2 | 20 | 8711.5624 | 8772 | 1.7016e-38 | 1.7016e-36 | CR | CR10 | 535027.19 | 213710.23 | 1.5 | 27.0585 | 0.40462 | 0.25005 | 0.6458 | 0.3229 | 27.7043 | 13.8521
CR | CR11 | 535321.62 | 214413.38 | 1.5 | 37.2 | 50.4988 | 32.5651 | 49.0356 | 36.3318 | 40.1789 | 50.4988 | 2 | 20 | 8709.5012 | 8773 | 4.6578e-38 | 4.6578e-36 | CR | CR11 | 535321.62 | 214413.38 | 1.5 | 37.201 | 1.4024 | 0.9402 | 2.3426 | 1.1713 | 39.5436 | 19.7718
CR | CR12 | 535110.94 | 214477.42 | 1.5 | 37.2 | 318.452 | 272.732 | 370.832 | 419.834 | 311.386 | 419.834 | 2 | 20 | 8340.166 | 8774 | 3.876e-22 | 3.876e-20 | CR | CR12 | 535110.94 | 214477.42 | 1.5 | 37.201 | 3.1566 | 1.6149 | 4.7716 | 2.3858 | 41.9726 | 20.9863
AR | AR1 | 534542.06 | 214282.58 | 1.5 | 37.2 | 272.075 | 219.814 | 266.631 | 150.373 | 210.939 | 272.075 | 2 | 20 | 8487.925 | 8775 | 2.0685e-25 | 2.0685e-23 | AR | AR1 | 534542.06 | 214282.58 | 1.5 | 29.6694 | 1.3656 | 0.44795 | 1.7494 | 0.87468 | 31.4187 | 15.7094
AR | AR2 | 534943.06 | 214357.58 | 1.5 | 37.2 | 776.033 | 884.345 | 943.935 | 1180.78 | 806.591 | 1180.78 | 2 | 20 | 7579.22 | 8776 | 3.4548e-14 | 3.4548e-12 | AR | AR2 | 534943.06 | 214357.58 | 1.5 | 29.6694 | 5.2285 | 1.3635 | 6.592 | 3.296 | 36.2614 | 18.1307
AR | AR3 | 535385.12 | 214556.22 | 1.5 | 37.2 | 56.6824 | 45.7946 | 53.1219 | 37.341 | 40.1789 | 56.6824 | 2 | 20 | 8703.3176 | 8777 | 9.3004e-37 | 9.3004e-35 | AR | AR3 | 535385.12 | 214556.22 | 1.5 | 37.201 | 1.3346 | 0.98204 | 2.3167 | 1.1583 | 39.5177 | 19.7588
AR | AR4 | 534804.56 | 214239.8 | 1.5 | 37.2 | 602.894 | 561.747 | 459.708 | 382.493 | 424.892 | 602.894 | 2 | 20 | 8157.106 | 8778 | 2.5958e-19 | 2.5958e-17 | AR | AR4 | 534804.56 | 214239.8 | 1.5 | 29.6694 | 4.139 | 0.84156 | 4.6601 | 2.33 | 34.3295 | 17.1647
AR | AR5 | 535044.19 | 214296.52 | 1.5 | 37.2 | 218.485 | 229.991 | 261.523 | 306.802 | 216.966 | 306.802 | 2 | 20 | 8453.198 | 8779 | 2.0195e-24 | 2.0195e-22 | AR | AR5 | 535044.19 | 214296.52 | 1.5 | 37.201 | 2.8459 | 1.0552 | 3.9011 | 1.9505 | 41.1021 | 20.5511
AR | AR6 | 534705.88 | 214368.02 | 1.5 | 37.2 | 766.758 | 718.467 | 789.677 | 456.166 | 820.654 | 820.654 | 2 | 20 | 7939.346 | 8780 | 6.1553e-17 | 6.1553e-15 | AR | AR6 | 534705.88 | 214368.02 | 1.5 | 29.6694 | 0.32779 | 0.29998 | 0.62479 | 0.3124 | 30.2942 | 15.1471
RR | RR1 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8792 | 3.2206e-38 | 3.2206e-36 | RR | RR1 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR2 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8793 | 4.4707e-38 | 4.4707e-36 | RR | RR2 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR3 | 535167 | 214292 | 1.5 | 37.2 | 73.1718 | 49.8652 | 76.6181 | 52.4793 | 50.2236 | 76.6181 | 2 | 20 | 8683.3819 | 8794 | 2.9187e-33 | 2.9187e-31 | RR | RR3 | 535167 | 214292 | 1.5 | 37.201 | 1.8418 | 0.98324 | 2.8251 | 1.4125 | 40.0261 | 20.013
RR | RR4 | 535312.38 | 213882.3 | 1.5 | 37.2 | 38.1318 | 41.724 | 40.863 | 26.2396 | 24.1073 | 41.724 | 2 | 20 | 8718.276 | 8795 | 2.0156e-36 | 2.0156e-34 | RR | RR4 | 535312.38 | 213882.3 | 1.5 | 27.0585 | 0.60492 | 0.37459 | 0.97951 | 0.48975 | 28.038 | 14.019
RR | RR5 | 535458.88 | 214569.02 | 1.5 | 37.2 | 43.2847 | 30.5297 | 40.863 | 30.2765 | 33.1476 | 43.2847 | 2 | 20 | 8716.7153 | 8796 | 4.367e-36 | 4.367e-34 | RR | RR5 | 535458.88 | 214569.02 | 1.5 | 37.201 | 1.116 | 0.84861 | 1.9646 | 0.98232 | 39.1656 | 19.5828
RR | RR6 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8797 | 1.8695e-35 | 1.8695e-33 | RR | RR6 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR7 | 534483.69 | 214428 | 1.5 | 37.2 | 226.729 | 167.914 | 222.703 | 121.106 | 187.836 | 226.729 | 2 | 20 | 8533.271 | 8798 | 4.2258e-26 | 4.2258e-24 | RR | RR7 | 534483.69 | 214428 | 1.5 | 29.6694 | 1.1231 | 0.38599 | 1.4348 | 0.71739 | 31.1041 | 15.5521
RR | RR8 | 535405.25 | 213931.3 | 1.5 | 37.2 | 31.9482 | 35.618 | 31.6688 | 23.212 | 28.1252 | 35.618 | 2 | 20 | 8724.382 | 8799 | 1.1696e-36 | 1.1696e-34 | RR | RR8 | 535405.25 | 213931.3 | 1.5 | 27.0585 | 0.57883 | 0.38693 | 0.96576 | 0.48288 | 28.0242 | 14.0121
RR | RR9 | 534645.56 | 214512 | 1.5 | 37.2 | 961.539 | 720.502 | 759.03 | 775.078 | 1009.49 | 1009.49 | 2 | 20 | 7750.51 | 8800 | 3.1687e-15 | 3.1687e-13 | RR | RR9 | 534645.56 | 214512 | 1.5 | 29.6694 | 1.8195 | 0.45358 | 2.273 | 1.1365 | 31.9424 | 15.9712
RR | RR10 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8801 | 4.6015e-35 | 4.6015e-33 | RR | RR10 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR11 | 535333 | 214355 | 1.5 | 37.2 | 37.1012 | 30.5297 | 46.9924 | 29.2673 | 37.1655 | 46.9924 | 2 | 20 | 8713.0076 | 8802 | 3.6745e-35 | 3.6745e-33 | RR | RR11 | 535333 | 214355 | 1.5 | 37.201 | 1.2306 | 0.85899 | 2.0896 | 1.0448 | 39.2906 | 19.6453
RR | RR12 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8803 | 8.8181e-37 | 8.8181e-35 | RR | RR12 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR13 | 535601.25 | 213994.69 | 1.5 | 37.2 | 29.8871 | 23.4061 | 24.5178 | 13.1198 | 21.0939 | 29.8871 | 2 | 20 | 8730.1129 | 8804 | 8.8001e-37 | 8.8001e-35 | RR | RR13 | 535601.25 | 213994.69 | 1.5 | 27.0585 | 0.50229 | 0.35932 | 0.86161 | 0.4308 | 27.9201 | 13.96
RR | RR14 | 535103.75 | 214597.11 | 1.5 | 37.2 | 696.678 | 771.385 | 831.562 | 923.433 | 632.817 | 923.433 | 2 | 20 | 7836.567 | 8805 | 7.4484e-16 | 7.4484e-14 | RR | RR14 | 535103.75 | 214597.11 | 1.5 | 37.201 | 2.4141 | 1.7131 | 4.1056 | 2.0528 | 41.3066 | 20.6533
RR | RR15 | 535372.44 | 214409.62 | 1.5 | 37.2 | 44.3153 | 29.5121 | 44.9493 | 32.2949 | 37.1655 | 44.9493 | 2 | 20 | 8715.0507 | 8806 | 5.6765e-35 | 5.6765e-33 | RR | RR15 | 535372.44 | 214409.62 | 1.5 | 37.201 | 1.1974 | 0.84807 | 2.0455 | 1.0227 | 39.2465 | 19.6232
RR | RR16 | 535220 | 214601.66 | 1.5 | 37.2 | 123.671 | 111.942 | 153.236 | 153.401 | 103.461 | 153.401 | 2 | 20 | 8606.599 | 8807 | 2.3934e-28 | 2.3934e-26 | RR | RR16 | 535220 | 214601.66 | 1.5 | 37.201 | 1.8734 | 1.4457 | 3.3191 | 1.6595 | 40.5201 | 20.26
RR | RR17 | 535203 | 214599.66 | 1.5 | 37.2 | 160.772 | 139.419 | 186.948 | 195.788 | 124.555 | 195.788 | 2 | 20 | 8564.212 | 8808 | 8.9337e-27 | 8.9337e-25 | RR | RR17 | 535203 | 214599.66 | 1.5 | 37.201 | 1.9471 | 1.4937 | 3.4408 | 1.7204 | 40.6418 | 20.3209
RR | RR18 | 535365.88 | 214341.17 | 1.5 | 37.2 | 38.1318 | 27.4768 | 43.9277 | 28.2581 | 35.1565 | 43.9277 | 2 | 20 | 8716.0723 | 8809 | 8.6938e-35 | 8.6938e-33 | RR | RR18 | 535365.88 | 214341.17 | 1.5 | 37.201 | 1.1014 | 0.79761 | 1.899 | 0.9495 | 39.1 | 19.55
RR | RR19 | 535189.19 | 213782.27 | 1.5 | 37.2 | 37.1012 | 46.8123 | 31.6688 | 28.2581 | 24.1073 | 46.8123 | 2 | 20 | 8713.1877 | 8810 | 1.999e-34 | 1.999e-32 | RR | RR19 | 535189.19 | 213782.27 | 1.5 | 27.0585 | 0.51201 | 0.31046 | 0.82247 | 0.41124 | 27.8809 | 13.9405
RR | RR20 | 535215 | 213810.02 | 1.5 | 37.2 | 36.0706 | 44.777 | 32.6904 | 32.2949 | 25.1118 | 44.777 | 2 | 20 | 8715.223 | 8811 | 1.6251e-34 | 1.6251e-32 | RR | RR20 | 535215 | 213810.02 | 1.5 | 27.0585 | 0.54765 | 0.32969 | 0.87734 | 0.43867 | 27.9358 | 13.9679
RR | RR21 | 535384.19 | 214421 | 1.5 | 37.2 | 45.3459 | 31.5474 | 46.9924 | 29.2673 | 36.161 | 46.9924 | 2 | 20 | 8713.0076 | 8812 | 2.9795e-34 | 2.9795e-32 | RR | RR21 | 535384.19 | 214421 | 1.5 | 37.201 | 1.1786 | 0.83903 | 2.0176 | 1.0088 | 39.2186 | 19.6093
RR | RR22 | 534482 | 214427 | 1.5 | 37.2 | 223.638 | 166.896 | 219.638 | 121.106 | 179.8 | 223.638 | 2 | 20 | 8536.362 | 8813 | 9.3117e-26 | 9.3117e-24 | RR | RR22 | 534482 | 214427 | 1.5 | 29.6694 | 1.1165 | 0.38443 | 1.4272 | 0.71361 | 31.0966 | 15.5483
RR | RR23 | 535670 | 214169 | 1.5 | 37.2 | 25.7647 | 20.3532 | 20.4315 | 14.129 | 20.0894 | 25.7647 | 2 | 20 | 8734.2353 | 8814 | 4.2091e-36 | 4.2091e-34 | RR | RR23 | 535670 | 214169 | 1.5 | 37.201 | 0.52096 | 0.42476 | 0.94572 | 0.47286 | 38.1467 | 19.0734
RR | RR24 | 534763.94 | 214555.36 | 1.5 | 37.2 | 1928.23 | 1307.69 | 1652.91 | 1464.37 | 1913.52 | 1928.23 | 2 | 20 | 6831.77 | 8815 | 2.4428e-10 | 2.4428e-08 | RR | RR24 | 534763.94 | 214555.36 | 1.5 | 29.6694 | 2.2217 | 0.51516 | 2.7331 | 1.3666 | 32.4025 | 16.2013
RR | RR25 | 534716.31 | 214558.59 | 1.5 | 37.2 | 1186.21 | 843.638 | 996.035 | 952.7 | 1087.84 | 1186.21 | 2 | 20 | 7573.79 | 8816 | 6.2421e-14 | 6.2421e-12 | RR | RR25 | 534716.31 | 214558.59 | 1.5 | 29.6694 | 2.1594 | 0.49836 | 2.6578 | 1.3289 | 32.3271 | 16.1636
RR | RR26 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8817 | 2.8435e-35 | 2.8435e-33 | RR | RR26 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR27 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8818 | 3.5563e-35 | 3.5563e-33 | RR | RR27 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR28 | 534796 | 213533.06 | 1.5 | 37.2 | 47.4071 | 42.7416 | 25.5394 | 4.0369 | 20.0894 | 47.4071 | 2 | 20 | 8712.5929 | 8819 | 1.3532e-33 | 1.3532e-31 | RR | RR28 | 534796 | 213533.06 | 1.5 | 29.0784 | 0.33906 | 0.23056 | 0.56962 | 0.28481 | 29.6481 | 14.824
RR | RR29 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8820 | 1.9402e-33 | 1.9402e-31 | RR | RR29 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR30 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8821 | 2.3146e-33 | 2.3146e-31 | RR | RR30 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR31 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8822 | 2.7564e-33 | 2.7564e-31 | RR | RR31 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR32 | 535256.69 | 213835.3 | 1.5 | 37.2 | 39.1624 | 43.7593 | 38.8198 | 29.2673 | 27.1207 | 43.7593 | 2 | 20 | 8716.2407 | 8823 | 1.3422e-33 | 1.3422e-31 | RR | RR32 | 535256.69 | 213835.3 | 1.5 | 27.0585 | 0.57325 | 0.34649 | 0.91974 | 0.45987 | 27.9782 | 13.9891
RR | RR33 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8824 | 3.8889e-33 | 3.8889e-31 | RR | RR33 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR34 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8825 | 4.6076e-33 | 4.6076e-31 | RR | RR34 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR35 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8826 | 5.4503e-33 | 5.4503e-31 | RR | RR35 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR36 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8827 | 6.4369e-33 | 6.4369e-31 | RR | RR36 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR37 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8828 | 7.5901e-33 | 7.5901e-31 | RR | RR37 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR38 | 535124.25 | 213698.91 | 1.5 | 37.2 | 38.1318 | 41.724 | 34.7335 | 21.1935 | 23.1029 | 41.724 | 2 | 20 | 8718.276 | 8829 | 2.7173e-33 | 2.7173e-31 | RR | RR38 | 535124.25 | 213698.91 | 1.5 | 27.0585 | 0.40981 | 0.25353 | 0.66334 | 0.33167 | 27.7218 | 13.8609
RR | RR39 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8830 | 4.2602e-34 | 4.2602e-32 | RR | RR39 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR40 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8831 | 1.2331e-32 | 1.2331e-30 | RR | RR40 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR41 | 535130.62 | 214595.33 | 1.5 | 37.2 | 436.969 | 464.052 | 535.305 | 593.419 | 404.802 | 593.419 | 2 | 20 | 8166.581 | 8832 | 8.2489e-19 | 8.2489e-17 | RR | RR41 | 535130.62 | 214595.33 | 1.5 | 37.201 | 2.2815 | 1.6753 | 3.9568 | 1.9784 | 41.1578 | 20.5789
RR | RR42 | 535424.62 | 213945.08 | 1.5 | 37.2 | 32.9788 | 31.5474 | 32.6904 | 21.1935 | 27.1207 | 32.9788 | 2 | 20 | 8727.0212 | 8833 | 1.0941e-33 | 1.0941e-31 | RR | RR42 | 535424.62 | 213945.08 | 1.5 | 27.0585 | 0.57722 | 0.38947 | 0.96669 | 0.48335 | 28.0252 | 14.0126
RR | RR43 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8834 | 9.0668e-34 | 9.0668e-32 | RR | RR43 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR44 | 535641 | 214086 | 1.5 | 37.2 | 30.9176 | 22.3885 | 23.4962 | 12.1106 | 22.0984 | 30.9176 | 2 | 20 | 8729.0824 | 8835 | 1.0897e-33 | 1.0897e-31 | RR | RR44 | 535641 | 214086 | 1.5 | 37.201 | 0.51678 | 0.39466 | 0.91143 | 0.45572 | 38.1124 | 19.0562
RR | RR45 | 535324.38 | 213889.3 | 1.5 | 37.2 | 38.1318 | 44.777 | 39.8414 | 25.2304 | 26.1163 | 44.777 | 2 | 20 | 8715.223 | 8836 | 1.4336e-32 | 1.4336e-30 | RR | RR45 | 535324.38 | 213889.3 | 1.5 | 27.0585 | 0.60372 | 0.3777 | 0.98143 | 0.49071 | 28.0399 | 14.0199
RR | RR46 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8837 | 3.1311e-32 | 3.1311e-30 | RR | RR46 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR47 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8838 | 3.64e-32 | 3.64e-30 | RR | RR47 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR48 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8839 | 4.2261e-32 | 4.2261e-30 | RR | RR48 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR49 | 535327 | 214389 | 1.5 | 37.2 | 44.3153 | 30.5297 | 48.014 | 30.2765 | 40.1789 | 48.014 | 2 | 20 | 8711.986 | 8840 | 4.9004e-32 | 4.9004e-30 | RR | RR49 | 535327 | 214389 | 1.5 | 37.201 | 1.3235 | 0.90432 | 2.2278 | 1.1139 | 39.4288 | 19.7144
RR | RR50 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8841 | 5.6751e-32 | 5.6751e-30 | RR | RR50 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR51 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8842 | 6.5643e-32 | 6.5643e-30 | RR | RR51 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR52 | 535457.69 | 214536.09 | 1.5 | 37.2 | 48.4376 | 31.5474 | 44.9493 | 33.3041 | 35.1565 | 48.4376 | 2 | 20 | 8711.5624 | 8843 | 7.5837e-32 | 7.5837e-30 | RR | RR52 | 535457.69 | 214536.09 | 1.5 | 37.201 | 1.1035 | 0.82283 | 1.9264 | 0.96318 | 39.1274 | 19.5637
RR | RR53 | 535200.06 | 213795.27 | 1.5 | 37.2 | 36.0706 | 43.7593 | 30.6472 | 30.2765 | 23.1029 | 43.7593 | 2 | 20 | 8716.2407 | 8844 | 4.1833e-32 | 4.1833e-30 | RR | RR53 | 535200.06 | 213795.27 | 1.5 | 27.0585 | 0.52878 | 0.31946 | 0.84824 | 0.42412 | 27.9067 | 13.9533
RR | RR54 | 535375 | 214402 | 1.5 | 37.2 | 41.2235 | 28.4944 | 42.9061 | 31.2857 | 36.161 | 42.9061 | 2 | 20 | 8717.0939 | 8845 | 4.1748e-32 | 4.1748e-30 | RR | RR54 | 535375 | 214402 | 1.5 | 37.201 | 1.1746 | 0.83721 | 2.0118 | 1.0059 | 39.2128 | 19.6064
RR | RR55 | 535541.12 | 213986.23 | 1.5 | 37.2 | 30.9176 | 23.4061 | 31.6688 | 16.1475 | 25.1118 | 31.6688 | 2 | 20 | 8728.3312 | 8846 | 8.6321e-33 | 8.6321e-31 | RR | RR55 | 535541.12 | 213986.23 | 1.5 | 27.0585 | 0.53463 | 0.37422 | 0.90885 | 0.45443 | 27.9673 | 13.9837
RR | RR56 | 535300.38 | 213874.3 | 1.5 | 37.2 | 41.2235 | 42.7416 | 40.863 | 26.2396 | 24.1073 | 42.7416 | 2 | 20 | 8717.2584 | 8847 | 5.6063e-32 | 5.6063e-30 | RR | RR56 | 535300.38 | 213874.3 | 1.5 | 27.0585 | 0.60336 | 0.37046 | 0.97382 | 0.48691 | 28.0323 | 14.0161
RR | RR57 | 535524.31 | 213984.5 | 1.5 | 37.2 | 30.9176 | 23.4061 | 32.6904 | 16.1475 | 27.1207 | 32.6904 | 2 | 20 | 8727.3096 | 8848 | 1.399e-32 | 1.399e-30 | RR | RR57 | 535524.31 | 213984.5 | 1.5 | 27.0585 | 0.54422 | 0.37888 | 0.9231 | 0.46155 | 27.9816 | 13.9908
RR | RR58 | 535384.19 | 214421 | 1.5 | 37.2 | 45.3459 | 31.5474 | 46.9924 | 29.2673 | 36.161 | 46.9924 | 2 | 20 | 8713.0076 | 8849 | 1.3299e-31 | 1.3299e-29 | RR | RR58 | 535384.19 | 214421 | 1.5 | 37.201 | 1.1786 | 0.83903 | 2.0176 | 1.0088 | 39.2186 | 19.6093
RR | RR59 | 535518.12 | 214441.09 | 1.5 | 37.2 | 40.1929 | 27.4768 | 36.7767 | 25.2304 | 28.1252 | 40.1929 | 2 | 20 | 8719.8071 | 8850 | 6.4584e-32 | 6.4584e-30 | RR | RR59 | 535518.12 | 214441.09 | 1.5 | 37.201 | 0.86218 | 0.66442 | 1.5266 | 0.7633 | 38.7276 | 19.3638
RR | RR60 | 534782.88 | 214562.19 | 1.5 | 37.2 | 2019.95 | 1462.37 | 1784.69 | 1611.72 | 2003.92 | 2019.95 | 2 | 20 | 6740.05 | 8851 | 6.7437e-10 | 6.7437e-08 | RR | RR60 | 534782.88 | 214562.19 | 1.5 | 29.6694 | 2.2942 | 0.54575 | 2.8399 | 1.42 | 32.5093 | 16.2546
RR | RR61 | 535670 | 214169 | 1.5 | 37.2 | 25.7647 | 20.3532 | 20.4315 | 14.129 | 20.0894 | 25.7647 | 2 | 20 | 8734.2353 | 8852 | 8.5274e-33 | 8.5274e-31 | RR | RR61 | 535670 | 214169 | 1.5 | 37.201 | 0.52096 | 0.42476 | 0.94572 | 0.47286 | 38.1467 | 19.0734
RR | RR62 | 535670 | 214169 | 1.5 | 37.2 | 25.7647 | 20.3532 | 20.4315 | 14.129 | 20.0894 | 25.7647 | 2 | 20 | 8734.2353 | 8853 | 1.0025e-32 | 1.0025e-30 | RR | RR62 | 535670 | 214169 | 1.5 | 37.201 | 0.52096 | 0.42476 | 0.94572 | 0.47286 | 38.1467 | 19.0734
RR | RR63 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8854 | 1.3164e-31 | 1.3164e-29 | RR | RR63 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR64 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8855 | 1.5121e-31 | 1.5121e-29 | RR | RR64 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR65 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8856 | 2.5826e-32 | 2.5826e-30 | RR | RR65 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR66 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8857 | 3.0063e-32 | 3.0063e-30 | RR | RR66 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR67 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8858 | 2.2023e-32 | 2.2023e-30 | RR | RR67 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR68 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8859 | 4.0577e-32 | 4.0577e-30 | RR | RR68 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR69 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8860 | 2.9881e-32 | 2.9881e-30 | RR | RR69 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR70 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8861 | 5.449e-32 | 5.449e-30 | RR | RR70 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR71 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8862 | 4.033e-32 | 4.033e-30 | RR | RR71 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR72 | 535456.12 | 213961.72 | 1.5 | 37.2 | 35.04 | 29.5121 | 33.712 | 21.1935 | 26.1163 | 35.04 | 2 | 20 | 8724.96 | 8863 | 1.9646e-31 | 1.9646e-29 | RR | RR72 | 535456.12 | 213961.72 | 1.5 | 27.0585 | 0.57036 | 0.38896 | 0.95932 | 0.47966 | 28.0178 | 14.0089
RR | RR73 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8864 | 8.4024e-32 | 8.4024e-30 | RR | RR73 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR74 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8865 | 9.6845e-32 | 9.6845e-30 | RR | RR74 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR75 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8866 | 7.2374e-32 | 7.2374e-30 | RR | RR75 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR76 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8867 | 1.2821e-31 | 1.2821e-29 | RR | RR76 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR77 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8868 | 1.4727e-31 | 1.4727e-29 | RR | RR77 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR78 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8869 | 9.4522e-31 | 9.4522e-29 | RR | RR78 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR79 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8870 | 1.0698e-30 | 1.0698e-28 | RR | RR79 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR80 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8871 | 1.2097e-30 | 1.2097e-28 | RR | RR80 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR81 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8872 | 2.5365e-31 | 2.5365e-29 | RR | RR81 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR82 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8873 | 1.9251e-31 | 1.9251e-29 | RR | RR82 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR83 | 535278.69 | 213854.3 | 1.5 | 37.2 | 37.1012 | 44.777 | 37.7983 | 28.2581 | 24.1073 | 44.777 | 2 | 20 | 8715.223 | 8874 | 2.4998e-30 | 2.4998e-28 | RR | RR83 | 535278.69 | 213854.3 | 1.5 | 27.0585 | 0.59011 | 0.35844 | 0.94855 | 0.47427 | 28.007 | 14.0035
RR | RR84 | 535253.38 | 214598.72 | 1.5 | 37.2 | 97.9059 | 77.342 | 113.395 | 103.949 | 74.3309 | 113.395 | 2 | 20 | 8646.605 | 8875 | 2.391e-27 | 2.391e-25 | RR | RR84 | 535253.38 | 214598.72 | 1.5 | 37.201 | 1.762 | 1.3545 | 3.1164 | 1.5582 | 40.3174 | 20.1587
RR | RR85 | 534733.88 | 214552.03 | 1.5 | 37.2 | 1318.12 | 875.186 | 1115.56 | 1022.34 | 1256.59 | 1318.12 | 2 | 20 | 7441.88 | 8876 | 7.1196e-13 | 7.1196e-11 | RR | RR85 | 534733.88 | 214552.03 | 1.5 | 29.6694 | 2.1515 | 0.47937 | 2.6308 | 1.3154 | 32.3002 | 16.1501
RR | RR86 | 535330 | 214374 | 1.5 | 37.2 | 41.2235 | 30.5297 | 49.0356 | 29.2673 | 38.1699 | 49.0356 | 2 | 20 | 8710.9644 | 8877 | 6.3072e-30 | 6.3072e-28 | RR | RR86 | 535330 | 214374 | 1.5 | 37.201 | 1.2794 | 0.88368 | 2.163 | 1.0815 | 39.364 | 19.682
RR | RR87 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8878 | 5.5605e-31 | 5.5605e-29 | RR | RR87 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR88 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8879 | 4.2712e-31 | 4.2712e-29 | RR | RR88 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR89 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8880 | 7.168e-31 | 7.168e-29 | RR | RR89 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR90 | 535072.25 | 214596.33 | 1.5 | 37.2 | 1082.12 | 1258.84 | 1215.67 | 1343.27 | 961.28 | 1343.27 | 2 | 20 | 7416.73 | 8881 | 1.0175e-12 | 1.0175e-10 | RR | RR90 | 535072.25 | 214596.33 | 1.5 | 37.201 | 2.6228 | 1.7489 | 4.2993 | 2.1497 | 41.5003 | 20.7502
RR | RR91 | 535642.12 | 213990.97 | 1.5 | 37.2 | 28.8565 | 21.3708 | 23.4962 | 13.1198 | 21.0939 | 28.8565 | 2 | 20 | 8731.1435 | 8882 | 9.2064e-31 | 9.2064e-29 | RR | RR91 | 535642.12 | 213990.97 | 1.5 | 27.0585 | 0.47601 | 0.34519 | 0.8212 | 0.4106 | 27.8797 | 13.9398
RR | RR92 | 535557.12 | 213989.23 | 1.5 | 37.2 | 30.9176 | 23.4061 | 28.6041 | 16.1475 | 24.1073 | 30.9176 | 2 | 20 | 8729.0824 | 8883 | 1.3366e-30 | 1.3366e-28 | RR | RR92 | 535557.12 | 213989.23 | 1.5 | 27.0585 | 0.52645 | 0.37057 | 0.89702 | 0.44851 | 27.9555 | 13.9777
RR | RR93 | 535578.12 | 213989.23 | 1.5 | 37.2 | 30.9176 | 23.4061 | 28.6041 | 15.1382 | 23.1029 | 30.9176 | 2 | 20 | 8729.0824 | 8884 | 1.5088e-30 | 1.5088e-28 | RR | RR93 | 535578.12 | 213989.23 | 1.5 | 27.0585 | 0.51329 | 0.36382 | 0.87711 | 0.43855 | 27.9356 | 13.9678
RR | RR94 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8885 | 1.2106e-29 | 1.2106e-27 | RR | RR94 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR95 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8886 | 1.3472e-29 | 1.3472e-27 | RR | RR95 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR96 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8887 | 1.4983e-29 | 1.4983e-27 | RR | RR96 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR97 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8888 | 1.6653e-29 | 1.6653e-27 | RR | RR97 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR98 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8889 | 1.4936e-30 | 1.4936e-28 | RR | RR98 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR99 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8890 | 2.4201e-30 | 2.4201e-28 | RR | RR99 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR100 | 535359.56 | 213908.88 | 1.5 | 37.2 | 38.1318 | 39.6887 | 39.8414 | 26.2396 | 28.1252 | 39.8414 | 2 | 20 | 8720.1586 | 8891 | 9.5981e-30 | 9.5981e-28 | RR | RR100 | 535359.56 | 213908.88 | 1.5 | 27.0585 | 0.59418 | 0.38431 | 0.97849 | 0.48924 | 28.0369 | 14.0185
RR | RR101 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8892 | 3.0564e-30 | 3.0564e-28 | RR | RR101 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR102 | 535370.75 | 213913.81 | 1.5 | 37.2 | 39.1624 | 39.6887 | 38.8198 | 25.2304 | 28.1252 | 39.6887 | 2 | 20 | 8720.3113 | 8893 | 1.1911e-29 | 1.1911e-27 | RR | RR102 | 535370.75 | 213913.81 | 1.5 | 27.0585 | 0.58951 | 0.38497 | 0.97448 | 0.48724 | 28.0329 | 14.0165
RR | RR103 | 535520.38 | 214477.55 | 1.5 | 37.2 | 41.2235 | 27.4768 | 38.8198 | 25.2304 | 31.1386 | 41.2235 | 2 | 20 | 8718.7765 | 8894 | 1.6452e-29 | 1.6452e-27 | RR | RR103 | 535520.38 | 214477.55 | 1.5 | 37.201 | 0.89649 | 0.68459 | 1.5811 | 0.79054 | 38.7821 | 19.391
RR | RR104 | 535648 | 214142 | 1.5 | 37.2 | 25.7647 | 22.3885 | 21.4531 | 14.129 | 19.085 | 25.7647 | 2 | 20 | 8734.2353 | 8895 | 3.0379e-30 | 3.0379e-28 | RR | RR104 | 535648 | 214142 | 1.5 | 37.201 | 0.53052 | 0.42197 | 0.95249 | 0.47624 | 38.1535 | 19.0767
RR | RR105 | 535639 | 214110 | 1.5 | 37.2 | 28.8565 | 24.4238 | 22.4746 | 15.1382 | 22.0984 | 28.8565 | 2 | 20 | 8731.1435 | 8896 | 4.83e-30 | 4.83e-28 | RR | RR105 | 535639 | 214110 | 1.5 | 37.201 | 0.52682 | 0.40866 | 0.93547 | 0.46774 | 38.1365 | 19.0682
RR | RR106 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8897 | 4.1904e-29 | 4.1904e-27 | RR | RR106 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR107 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8898 | 4.6289e-29 | 4.6289e-27 | RR | RR107 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR108 | 534708 | 213515.94 | 1.5 | 37.2 | 45.3459 | 47.8299 | 19.4099 | 6.0553 | 19.085 | 47.8299 | 2 | 20 | 8712.1701 | 8899 | 5.1105e-29 | 5.1105e-27 | RR | RR108 | 534708 | 213515.94 | 1.5 | 29.0784 | 0.35783 | 0.24004 | 0.59787 | 0.29894 | 29.6763 | 14.8382
RR | RR109 | 535322 | 214570 | 1.5 | 37.2 | 65.9576 | 48.8476 | 69.4671 | 52.4793 | 46.2057 | 69.4671 | 2 | 20 | 8690.5329 | 8900 | 4.5039e-28 | 4.5039e-26 | RR | RR109 | 535322 | 214570 | 1.5 | 37.201 | 1.561 | 1.1485 | 2.7096 | 1.3548 | 39.9106 | 19.9553
RR | RR110 | 535159 | 214598.66 | 1.5 | 37.2 | 277.228 | 297.156 | 343.249 | 372.401 | 254.131 | 372.401 | 2 | 20 | 8387.599 | 8901 | 6.5417e-21 | 6.5417e-19 | RR | RR110 | 535159 | 214598.66 | 1.5 | 37.201 | 2.1319 | 1.6075 | 3.7394 | 1.8697 | 40.9404 | 20.4702
RR | RR111 | 535387.5 | 213925.69 | 1.5 | 37.2 | 32.9788 | 37.6533 | 35.7551 | 24.2212 | 28.1252 | 37.6533 | 2 | 20 | 8722.3467 | 8902 | 2.4745e-29 | 2.4745e-27 | RR | RR111 | 535387.5 | 213925.69 | 1.5 | 27.0585 | 0.58695 | 0.38836 | 0.97531 | 0.48765 | 28.0338 | 14.0169
RR | RR112 | 534599 | 214496 | 1.5 | 37.2 | 766.758 | 595.33 | 612.945 | 586.355 | 835.721 | 835.721 | 2 | 20 | 7924.279 | 8903 | 7.3534e-16 | 7.3534e-14 | RR | RR112 | 534599 | 214496 | 1.5 | 29.6694 | 1.4222 | 0.45883 | 1.8811 | 0.94053 | 31.5504 | 15.7752
RR | RR113 | 534453.69 | 214398.55 | 1.5 | 37.2 | 172.108 | 134.331 | 164.473 | 84.7742 | 103.461 | 172.108 | 2 | 20 | 8587.892 | 8904 | 9.3548e-25 | 9.3548e-23 | RR | RR113 | 534453.69 | 214398.55 | 1.5 | 29.6694 | 0.95548 | 0.34899 | 1.25 | 0.625 | 30.9194 | 15.4597
RR | RR114 | 534538.88 | 214467.92 | 1.5 | 37.2 | 423.572 | 286.98 | 360.616 | 275.516 | 471.097 | 471.097 | 2 | 20 | 8288.903 | 8905 | 1.7861e-19 | 1.7861e-17 | RR | RR114 | 534538.88 | 214467.92 | 1.5 | 29.6694 | 1.2061 | 0.42897 | 1.5602 | 0.78008 | 31.2295 | 15.6148
RR | RR115 | 534516.25 | 214460.61 | 1.5 | 37.2 | 338.033 | 227.955 | 279.911 | 193.77 | 380.695 | 380.695 | 2 | 20 | 8379.305 | 8906 | 1.0199e-20 | 1.0199e-18 | RR | RR115 | 534516.25 | 214460.61 | 1.5 | 29.6694 | 1.1905 | 0.41989 | 1.5297 | 0.76484 | 31.199 | 15.5995
RR | RR116 | 534686.5 | 214539.06 | 1.5 | 37.2 | 1068.72 | 827.356 | 846.885 | 888.111 | 1064.74 | 1068.72 | 2 | 20 | 7691.28 | 8907 | 3.5182e-14 | 3.5182e-12 | RR | RR116 | 534686.5 | 214539.06 | 1.5 | 29.6694 | 2.2016 | 0.47498 | 2.6708 | 1.3354 | 32.3402 | 16.1701
RR | RR117 | 534559.56 | 214479.97 | 1.5 | 37.2 | 545.181 | 387.728 | 451.536 | 384.512 | 593.643 | 593.643 | 2 | 20 | 8166.357 | 8908 | 4.9825e-18 | 4.9825e-16 | RR | RR117 | 534559.56 | 214479.97 | 1.5 | 29.6694 | 1.1968 | 0.44364 | 1.6404 | 0.82021 | 31.3098 | 15.6549
RR | RR118 | 534579.62 | 214493.19 | 1.5 | 37.2 | 669.882 | 504.758 | 526.111 | 501.581 | 727.238 | 727.238 | 2 | 20 | 8032.762 | 8909 | 1.0084e-16 | 1.0084e-14 | RR | RR118 | 534579.62 | 214493.19 | 1.5 | 29.6694 | 1.3021 | 0.45947 | 1.7616 | 0.88081 | 31.431 | 15.7155
RR | RR119 | 535173.69 | 213760.16 | 1.5 | 37.2 | 36.0706 | 45.7946 | 33.712 | 24.2212 | 26.1163 | 45.7946 | 2 | 20 | 8714.2054 | 8910 | 1.2101e-28 | 1.2101e-26 | RR | RR119 | 535173.69 | 213760.16 | 1.5 | 27.0585 | 0.48364 | 0.29543 | 0.77907 | 0.38953 | 27.8375 | 13.9188
RR | RR120 | 535071.94 | 213690.45 | 1.5 | 37.2 | 46.3765 | 41.724 | 32.6904 | 18.1659 | 26.1163 | 46.3765 | 2 | 20 | 8713.6235 | 8911 | 1.4614e-28 | 1.4614e-26 | RR | RR120 | 535071.94 | 213690.45 | 1.5 | 27.0585 | 0.39326 | 0.24062 | 0.63063 | 0.31532 | 27.6891 | 13.8445
RR | RR121 | 535659 | 214261 | 1.5 | 37.2 | 28.8565 | 21.3708 | 28.6041 | 18.1659 | 21.0939 | 28.8565 | 2 | 20 | 8731.1435 | 8912 | 2.6922e-29 | 2.6922e-27 | RR | RR121 | 535659 | 214261 | 1.5 | 37.201 | 0.55348 | 0.46767 | 1.0212 | 0.51058 | 38.2222 | 19.1111
RR | RR122 | 535677 | 214232 | 1.5 | 37.2 | 27.8259 | 18.3178 | 30.6472 | 16.1475 | 22.0984 | 30.6472 | 2 | 20 | 8729.3528 | 8913 | 3.6632e-29 | 3.6632e-27 | RR | RR122 | 535677 | 214232 | 1.5 | 37.201 | 0.52973 | 0.44659 | 0.97632 | 0.48816 | 38.1773 | 19.0887
RR | RR123 | 535184 | 214599.66 | 1.5 | 37.2 | 211.271 | 190.302 | 245.178 | 258.359 | 175.783 | 258.359 | 2 | 20 | 8501.641 | 8914 | 1.1789e-22 | 1.1789e-20 | RR | RR123 | 535184 | 214599.66 | 1.5 | 37.201 | 2.0223 | 1.544 | 3.5664 | 1.7832 | 40.7674 | 20.3837
RR | RR124 | 535239 | 214601.66 | 1.5 | 37.2 | 104.089 | 86.5009 | 125.654 | 121.106 | 78.3488 | 125.654 | 2 | 20 | 8634.346 | 8915 | 9.875e-26 | 9.875e-24 | RR | RR124 | 535239 | 214601.66 | 1.5 | 37.201 | 1.8031 | 1.3934 | 3.1965 | 1.5983 | 40.3975 | 20.1988
RR | RR125 | 535033.5 | 214591.97 | 1.5 | 37.2 | 2001.4 | 2442.38 | 2090.14 | 2353.49 | 1761.84 | 2442.38 | 2 | 20 | 6317.62 | 8916 | 2.2137e-08 | 2.2137e-06 | RR | RR125 | 535033.5 | 214591.97 | 1.5 | 37.201 | 2.7498 | 1.8179 | 4.5678 | 2.2839 | 41.7688 | 20.8844
RR | RR126 | 535507.31 | 213975.5 | 1.5 | 37.2 | 32.9788 | 27.4768 | 34.7335 | 20.1843 | 28.1252 | 34.7335 | 2 | 20 | 8725.2665 | 8917 | 8.0976e-29 | 8.0976e-27 | RR | RR126 | 535507.31 | 213975.5 | 1.5 | 27.0585 | 0.54824 | 0.37965 | 0.92789 | 0.46395 | 27.9864 | 13.9932
RR | RR127 | 535146.44 | 213724.45 | 1.5 | 37.2 | 37.1012 | 45.7946 | 34.7335 | 21.1935 | 25.1118 | 45.7946 | 2 | 20 | 8714.2054 | 8918 | 2.523e-28 | 2.523e-26 | RR | RR127 | 535146.44 | 213724.45 | 1.5 | 27.0585 | 0.43993 | 0.27117 | 0.7111 | 0.35555 | 27.7696 | 13.8848
RR | RR128 | 535339.06 | 213898.95 | 1.5 | 37.2 | 38.1318 | 42.7416 | 39.8414 | 25.2304 | 25.1118 | 42.7416 | 2 | 20 | 8717.2584 | 8919 | 2.0931e-28 | 2.0931e-26
Note on AE2: Ben Madge: nox to NO2 conversion factor

## 5-Rslts LT NOx
Results - Annual Mean NOx
NO2
[7 empty] | 18.6005 | Thermal Plant | Gen Sets | All Plant
|  | Exposure | Receptor name | X(m) | Y(m) | Z(m) | BG NOx | AM NOx PC | AM NOx PC after Adjust | AM NOx PC | PC as a % of AQO | PEC NOx | PEC as a % of AQO | Less tha 1% (Statutory Sites)/100% (LWS)? | Nitrogen Deposition (kg/ha/yr) | Critical Load | %CL | Acid Deposition (keq/ha/yr) | Critical Load | % CL
| 1 | ER | ER1 | 537428.62 | 213290.5 | 0 | 14.0525 | 0.23799 | 0.0042281 | 0.24222 | 0.80739 | 14.2947 | 47.6489 | Yes | 2.0584 | 15 | 13.7229 | 0.15 | 1.11 | 13.2
| 1 | ER | ER2 | 538389.44 | 210732 | 0 | 17.2156 | 0.081309 | 0.0017549 | 0.083064 | 0.27688 | 17.2987 | 57.6623 | Yes | 2.491 | 8 | 31.1377 | 0.18 | 1.11 | 16
| 1 | ER | ER3 | 536844.12 | 204773.66 | 0 | 18.7146 | 0.026309 | 0.0007585 | 0.027067 | 0.090224 | 18.7417 | 62.4723 | Yes | 2.6988 | 15 | 17.992 | 0.19 | 1.11 | 17.3
| 1 | ER | ER4 | 535207.75 | 208992.55 | 0 | 15.6757 | 0.056165 | 0.0018256 | 0.057991 | 0.1933 | 15.7337 | 52.4457 | Yes | 2.2657 | 15 | 15.1044 | 0.16 | 1.75 | 9.3
| 1 | ER | ER5 | 532430.31 | 207691 | 0 | 12.9003 | 0.068133 | 0.0018328 | 0.069966 | 0.23322 | 12.9702 | 43.2341 | Yes | 1.8677 | 15 | 12.4514 | 0.13 | 1.75 | 7.6
| 1 | ER | ER6 | 532011.44 | 206625.62 | 0 | 14.2379 | 0.05607 | 0.0015019 | 0.057571 | 0.1919 | 14.2955 | 47.6516 | Yes | 2.0585 | 15 | 13.7237 | 0.15 | 2.1 | 7
| 1 | LWS | LWS1 | 536412.12 | 214101.48 | 0 | 19.5244 | 0.011018 | 0.58107 | 0.58107 | 1.9369 | 20.1055 | 67.0183 | Yes | 2.8952 | 5 | 57.9038 | 0.21 | 1.23 | 16.8
| 1 | LWS | LWS2 | 536048.38 | 213873.66 | 0 | 18.0287 | 0.013508 | 0.73213 | 0.73213 | 2.4404 | 18.7609 | 62.5363 | Yes | 2.7016 | 5 | 54.0313 | 0.19 | 1.23 | 15.4472
| 1 | LWS | LWS3 | 536012.38 | 213350.44 | 0 | 18.0287 | 0.010533 | 0.48595 | 0.48595 | 1.6198 | 18.5147 | 61.7157 | Yes | 2.6661 | 5 | 53.3223 | 0.19 | 1.23 | 15.4472
| 1 | LWS | LWS4 | 534701.69 | 213374.95 | 0 | 19.9714 | 0.021344 | 0.70513 | 0.70513 | 2.3504 | 20.6766 | 68.9219 | Yes | 2.9774 | 5 | 59.5485 | 0.21 | 1.2 | 17.5
| 1 | LWS | LWS5 | 534068 | 214494 | 0 | 20.5161 | 0.035673 | 0.78201 | 0.78201 | 2.6067 | 21.2981 | 70.9937 | Yes | 3.0669 | 5 | 61.3385 | 0.22 | 1.2 | 18.3333
| 1 | LWS | LWS6 | 536177 | 213761.58 | 0 | 18.0287 | 0.011362 | 0.60883 | 0.60883 | 2.0294 | 18.6376 | 62.1253 | Yes | 2.6838 | 5 | 53.6762 | 0.19 | 1.23 | 15.4472
| 1 | LWS | LWS7 | 535169 | 213657 | 0 | 18.4635 | 0.024488 | 0.90158 | 0.90158 | 3.0053 | 19.3651 | 64.5503 | Yes | 2.7886 | 5 | 55.7714 | 0.2 | 1.23 | 16.2602
| 1 | LWS | LWS8 | 535673 | 213828 | 0 | 18.4635 | 0.020797 | 0.95728 | 0.95728 | 3.1909 | 19.4208 | 64.7359 | Yes | 2.7966 | 5 | 55.9318 | 0.2 | 1.23 | 16.2602
| 1 | LWS | LWS9 | 534789.56 | 214231.94 | 0 | 20.5161 | 0.22021 | 7.1791 | 7.1791 | 23.9302 | 27.6952 | 92.3172 | Yes | 3.9881 | 5 | 79.7621 | 0.28 | 1.33 | 21.0526
| 1 | LWS | LWS10 | 533562.88 | 213867.77 | 0 | 18.4238 | 0.009559 | 0.27993 | 0.27993 | 0.93308 | 18.7038 | 62.3459 | Yes | 2.6933 | 5 | 53.8668 | 0.19 | 1.33 | 14.2857
| 1 | LWS | LWS11 | 534375.19 | 214135 | 0 | 20.5161 | 0.047267 | 1.3667 | 1.3667 | 4.5556 | 21.8828 | 72.9426 | Yes | 3.1511 | 5 | 63.0224 | 0.23 | 1.33 | 17.2932
Note on I3: Ben Madge: nox to NO2 conversion factor

## 6-Rslts ST NOx
Results - 100 Percentile 24 Hour Mean NOx
NO2
[6 empty] | 18.6005 | Thermal Plant
| Exposure | Receptor name | X(m) | Y(m) | Z(m) | BG NOx | ST NOx PC | PC as a % of AQO | PEC NOx | PEC as a % of AQO | Less tha 10% (Statutory Sites)/100% (LWS)?
| ER | ER1 | 537428.62 | 213290.5 | 0 | 14.0525 | 2.3749 | 3.1665 | 16.4273 | 21.9031 | Yes
| ER | ER2 | 538389.44 | 210732 | 0 | 17.2156 | 1.4783 | 1.9711 | 18.694 | 24.9253 | Yes
| ER | ER3 | 536844.12 | 204773.66 | 0 | 18.7146 | 0.4707 | 0.6276 | 19.1853 | 25.5804 | Yes
| ER | ER4 | 535207.75 | 208992.55 | 0 | 15.6757 | 1.0857 | 1.4475 | 16.7614 | 22.3485 | Yes
| ER | ER5 | 532430.31 | 207691 | 0 | 12.9003 | 0.95593 | 1.2746 | 13.8562 | 18.4749 | Yes
| ER | ER6 | 532011.44 | 206625.62 | 0 | 14.2379 | 0.80514 | 1.0735 | 15.043 | 20.0574 | Yes
| LWS | LWS1 | 536412.12 | 214101.48 | 0 | 19.5244 | 5.0168 | 6.689 | 24.5412 | 32.7216 | Yes
| LWS | LWS2 | 536048.38 | 213873.66 | 0 | 18.0287 | 6.3127 | 8.4169 | 24.3414 | 32.4552 | Yes
| LWS | LWS3 | 536012.38 | 213350.44 | 0 | 18.0287 | 5.8267 | 7.7689 | 23.8554 | 31.8072 | Yes
| LWS | LWS4 | 534701.69 | 213374.95 | 0 | 19.9714 | 9.56 | 12.7467 | 29.5314 | 39.3752 | Yes
| LWS | LWS5 | 534068 | 214494 | 0 | 20.5161 | 14.7317 | 19.6423 | 35.2478 | 46.9971 | Yes
| LWS | LWS6 | 536177 | 213761.58 | 0 | 18.0287 | 5.6996 | 7.5995 | 23.7284 | 31.6379 | Yes
| LWS | LWS7 | 535169 | 213657 | 0 | 18.4635 | 12.8852 | 17.1803 | 31.3487 | 41.7983 | Yes
| LWS | LWS8 | 535673 | 213828 | 0 | 18.4635 | 9.1861 | 12.2481 | 27.6496 | 36.8661 | Yes
| LWS | LWS9 | 534789.56 | 214231.94 | 0 | 20.5161 | 93.1268 | 124.1691 | 113.6429 | 151.5239 | No
| LWS | LWS10 | 533562.88 | 213867.77 | 0 | 18.4238 | 6.1486 | 8.1981 | 24.5724 | 32.7633 | Yes
| LWS | LWS11 | 534375.19 | 214135 | 0 | 20.5161 | 20.8048 | 27.7397 | 41.3209 | 55.0945 | Yes
Note on I3: Ben Madge: nox to NO2 conversion factor