## Sheet1
Environmental Assessment of the Chiller System for the provision of Chilled water for process cooling - March 2022 | [9 empty] | HS057 - Environmental Assessment of Chillers - A1
Location | Hazard Source | Failure leading to loss of containment | Failure details | Pathway | Receptor | Consequences | Likelihood of Exposure | Consequence of exposure | Overall Risk | Control Measures in place | Additional Control Measures
Chiller Tank for Water | External Tank Filling | Failure of fill pipework | Splitting of pipework. Failure of valve to open. Splitting of delivery pipework. Leaking flange or connection. Vehicle fire. Tanker rupture. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | Medium | Medium | Pipe work Inspection Program. | Refresh formal shutdown procedures as part of the environmental management system. Ensure the tank is inspected regularly. Alarm system to be introduced.
Chiller pipework | Pipework or pumps | Regular circulation of water in a closed loop system. Some Water treatment chemicals in the water. | Part of regular chiller activity. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | Low | Low | Maintain the system and address any leaks. | Additional alarms for High/High tank level to show overflowing or low/low to show leak.
Chiller | Chiller operation | Noise emission. | Part of regular chiller activity. | Local environment. | Local environment | Local noise. | Low | Low | Low | Maintaining the pumps and equipment. | Consider pumps to be placed inside cabinets.
Chiller | Chemical dosing | Pump leak or leak from chemical drum. | Rupture | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | Low | Low | Regular checks. | Bund for chemicals.
Chiller | Cooling Coil Blowdown | Clearing of the cooling coil with compressed air. | Regular blow out to clear cold water before steam is introduced. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | Low | Low | None