## Sheet1
Environmental Assessment of MDI Use | [9 empty] | HS061 - Environmental Assessment of MDI Use - A1
Location | Hazard Source | Failure leading to loss of containment | Failure details | Pathway | Receptor | Consequences | Likelihood of Exposure | Consequence of exposure | Overall Risk | Control Measures in place | Additional Control Measures
External Bulk Tank Farm | External Tank structure | Failure of containment tank | Splitting of tank material. Rupture of weld or flange. Heavy snow. Ice build up. | Into bunded area with 110% tank volume capacity. | Ground, Groundwater, Surface Water | Run off site. Solvent free MDI diisocyanate. Harmful if ingested and a skin sensitizer. Needs to be protected from moisture or CO2 is released which can result in pressurisation of the packaging. | Low | High | Medium | Trace heating. Bund wall. Adequate bund capacity. Spill kit available. | Tank Inspection Program. Bund Inspection Program. Inspection of bund pipework seals. Emergency Action Plan for safe transfer/collection of material. Ensure all bund walls are suitably sealed around pipework.
External Bulk Tank Farm | External Tank Filling | Failure of fill pipework | Splitting of pipework. Failure of valve to open. Splitting of delivery pipework. Leaking flange or connection. Vehicle fire. Tanker rupture. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | High | Medium | Pipe work Inspection Program. Concrete Tanker pad is sloped to contain a small spill. All deliveries are attended to identify any issues. Spill Kits provided. Tank filling is carried out once a month and takes about 3 hours to discharge the load. | Bund fill alarms. Refresh formal filling and spill response procedures as part of the environmental management system.
External Bulk Tank Farm | Failure of containment bund | Major damage from vehicle impact. Subsidence. | Cracking of bund walls. Impact of adjacent linked structures. Ground movement. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | High | Medium | Security fencing, concrete kerbs. Attended reversing. | Inspection of Bunds. Removal of lighting gantry and making separate from the bund wall structure.
External Bulk Tank Farm | Failure of pipe sealing | Failure of bund pipe seals | Splitting around point where pipes pass through bund wall. | Through bund walls. Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | Low | Low | Low | Visual inspection | Inspection of Bunds. Assessment of seals for Fire resistance.
IBC or Drum Delivery | Spill/leak | Rupture of IBC or Drum | Spill/leak | From FLT when being transported directly onto hard concrete surfaces. | Ground, Groundwater, Surface Water, employees, visitors, adjacent tenants, roadways around the site. | Run off site. | Low | Medium | Medium | Site is secure when not occupied. CCTV has extensive coverage. Viscosity is high and liquid is slow flowing. At 0°C part crystalisation will occur. Protect from moisture as ingress can release CO2 and cause packaging rupture. | Improve site security when site is occupied. Improve Goods in Barrier to prevent access underneath. Finish off Security fencing around the tank farm. Ensure all fencing is secured. Key control systems in place.
External Bulk Tank Farm | Drain valves/pipe work tampered with. | Vandalism | Drain valves/pipe work tampered with. | Into bunded area with 110% tank volume capacity. | Ground, Groundwater, Surface Water | Run off site. | Low | High | Medium | Site is secure when not occupied. CCTV has extensive coverage. | Improve site security when site is occupied. Improve Goods in Barrier to prevent access underneath. Finish off Security fencing around the tank farm. Ensure all fencing is secured. Key control systems in place. Ensure any drain valves are sealed with a blank flange. Avoid using quick release hoses. Lock off any local controls that allow pumps to be operated.
Process area | Decanting to charge vessels. | Pump or pipework leak. | Splitting of pipe work or pump leak causing small localised spillage. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Local spill - limited pathway beyond local process area. | Low | Low | Low | Spill Kits. Operators present when decanting the product.
Process area | Pipework blockage/burst. | Freezing of product. | Splitting of pipework/pump glands. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Local spill - limited pathway beyond local process area. | Low | Low | Low | Management of tank temperatures between 20°C & 40 °C.
Process or Storage area | Product | Moisture ingress into the packaging. | Over pressurisation of the packaging and potential burst. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Local spill - limited pathway beyond local process area. | Low | Low | Low | Appropriate storage. Prevention of moisture ingress. Careful selection of packaging. Inspection of the packaging. | Indoor storage. Shrink wrap.