## Sheet1
Environmental Assessment of Tanker Filling | [9 empty] | HS063 - Environmental Assessment of Tanker Filling - A1
Location | Hazard Source | Failure leading to loss of containment | Failure details | Pathway | Receptor | Consequences | Likelihood of Exposure | Consequence of exposure | Overall Risk | Control Measures in place | Additional Control Measures
Tanker Discharge Point | Flammable liquid | Pipework rupture | Puncture or split at discharge pipework. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. Fire. Flash fire. Running Fire. | High | Medium | Medium | 1.5m3 Drain pit for initial containment. Shut off valve. Stop pump. Evacuate the area immediately. Alert others. Alert the Spill Team. | Contain the spill. Plan the approach.
Tanker Discharge Point | Non-flammable liquid | Pipework rupture | Puncture or split at point of impact. | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | High | Medium | Medium | 1.5m3 Drain pit for initial containment. Shut off valve. Stop pump. Evacuate the area immediately. Alert others. Alert the Spill Team. | Contain the spill. Plan the approach.
Tanker Discharge Point | Flammable liquid | Tanker rupture | Tanker rupture | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. Fire. Flash fire. Running Fire. | High | Medium | Medium | 1.5m3 Drain pit for initial containment. Shut off valve. Stop pump. Evacuate the area immediately. Full site evacuation. Call Fire & Rescue Service. | Contain the spill. Plan the approach.
Tanker Discharge Point | Non-flammable liquid | Tanker rupture | Tanker rupture | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site. | High | Medium | Medium | 1.5m3 Drain pit for initial containment. Shut off valve. Stop pump. Evacuate the area immediately. Alert others. Alert the Spill Team. Contain the spill. Call the Fire & Rescue Service. | Contain the spill. Plan the approach.
Tanker Discharge Point | Leak | Pipework or Tanker rupture when bund is full of rainwater. | Pipework or Tanker rupture | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site | High | High | High | Ensure that the containment pit is empty before tanker filling commences. | Follow the rainwater pumping procedure.
Front Tanker Discharge Point | Leak | Pipework or Tanker rupture when valve is open and spill runs to drain. | Pipework or Tanker rupture | Over concrete surfaces. | Ground, Groundwater, Surface Water | Run off site | High | High | High | Ensure that the driver understands how to operate the valve in the event of a spill to that it is contained within the pit. | Display signage. Make valve automatic.
Tanker Discharge Point | Noise | Engine operation. | Running noisy | In local area. | Local residents, tenants. | Local area. | Low | Low | Low | Keep tanker deliveries to business hours. | Highlight any noisy equipment to drivers.