## Assumptions
Modelling Assumptions and Parameters
SoundPLAN® acoustic modelling software (version 9.1) implementing the calculation procedures of ISO 9613 has been employed to predict the propagation of sound from the Proposed Development in all directions and to quantify resultant sound levels at the identified noise-sensitive receptor locations.
All plant and operational assumptions have been derived from a review by AECOM of vendor specification data sheets.
Embedded noise mitigation measures have been built into the data centre design in the form of attenuators for the louvres and exhaust fans. Insertion loss data has been obtained from manufacturer specification sheets
Q-nis LDM Acoustic Module 4500x2200x2700 mm attenuators for all Gen side louvres on both data centre buildings; Q-nis LDM Acoustic Module 4500x2800x1600 mm attenuators for all non-Gen side louvres on both data centre buildings; and Danaan Air DH Extract Unit 1200 mm with fan flow grids for all exhaust fans on both data centre buildings
Emergency operation of the Proposed Development has been assumed to be continuous through the day and night
Generator testing and maintenance has been confirmed to solely take place during the daytime, so a night-time assessment has not been undertaken
The ground absorption has been set to 1 (i.e. assumed soft ground conditions), except where identifiable ground features are present where acoustically hard ground (such as water and industrial estates) is set to 0
Topography obtained from DEFRA LIDAR data has been used
Building footprints in the surrounding area have been sourced from Ordnance Survey Open Map data
Heights of residential buildings have been standardised from OS building height data and checked against aerial photography for assessed receptors
Receiver points have been modelled as 1.5 m above local ground level
The maximum order of reflections was 3
Grid Noise Map Spacing 10 m at 1.5 m height above ground
Site Building Heights
Building | Building Height
Data Centre A & B | 17.9m
Data Centre A & B MV Rooms | 6.0m
Site Acoustic Barriers
For the parapets, they are modelled as noise barriers in the SoundPLAN model. As confirmed by the architects, the parapet walls are imperforate (solid). More details on the design will be developed during the detailed design stage.