## Source Noise Data
Data Centre A
Plant Number | Plant quantity | Plant Name (Source Data) | Source Height | Total A-Weighted Sound Power Level dBA | Unweighted dB at Octave Band Centre Frequency (Hz)
[5 empty] | Total Unweighted Sound Power Level dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
1 | 6 | Fresh Air Intake Louvre non-Gen side (Sound Power Level per m2) | 3.0m on façade | 81.81 | 90.4394 | 86.3 | 83.1 | 81.6 | 83.3 | 74.5 | 76 | 76.4 | 67.4 | 53.5
2 | 6 | Fresh Air Intake Louvre Gen side (Sound Power Level per m2) | 3.0m on façade | 79.46 | 87.956 | 83.7 | 80.6 | 77.9 | 81.6 | 72.8 | 74.2 | 73.3 | 63.8 | 41.7
3 | 76 | Exhaust Fan (Single and 2-storey) | 4.0m | 84.3 | 111.2206 | 105.3 | 102.1 | 105.6 | 104 | 101.2 | 97.5 | 92 | 86.3 | 80.2
4 | 4 | VRF Condensers | At roof level (17.9m) | 72.97 | 83.0917 |  | 81.5 | 71.5 | 74 | 72 | 67 | 62.5 | 56.5 | 53
5 | 11 | Split Unit condensers | 1.5m | 67.33 | 67.1488 |  | 37.2 | 43.5 | 49.1 | 53.5 | 56.9 | 60.9 | 61.9 | 62
6 | 1 | Toilet Exhaust Fan | At roof level (17.9m) | 75.25 | 77.4803 |  | 63 | 68 | 69 | 73 | 70 | 69 | 62 | 54
7 | 1 | Admin AHU (Air Inlet) | At roof level (17.9m) | 55.83 | 68.6595 |  | 58 | 68 | 51 | 52 | 47 | 45 | 44 | 41
8 | 1 | Admin AHU (Air Exhaust) | At roof level (17.9m) | 88.73 | 89.9632 |  | 73 | 81 | 76 | 84 | 85 | 81 | 80 | 71
9 | 1 | Admin AHU (Breakout) | 2.4m | 54.62 | 74.7613 |  | 65 | 70 | 66 | 67 | 64 | 67 | 54 | 31
10 | 56 | CRAC Condensers | At roof level (17.9m) | 80.72 | 94.2365 |  |  | 93.8 | 83.3 | 73.6 | 70.5 | 66.6 | 59.4 | 54.4
11 | 2 | Transformers (80MVA) provided by AECOM Electrical team | 2.0m | 74 | 83.6039 |  | 70.4 | 81.3 | 77.5 | 74 | 61.1 | 52.5 | 53.7 | 55.8
Plant Number | Plant quantity | Plant Name (Source Data) |  | Source Height | Total A-Weighted Sound Power Level dBA | Unweighted dB at Octave Band Centre Frequency (Hz)
[6 empty] | Total Unweighted Sound Power Level dB | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
11 | 15 | Generator 75 dB | LHS | 5.0m | 91.68 | 102.3722 | 95 | 100.9 | 86.6 | 87.3 | 84.2 | 83.6 | 78.1 | 84
|  |  | RHS |  | 91.68 | 102.3722 | 95 | 100.9 | 86.6 | 87.3 | 84.2 | 83.6 | 78.1 | 84
|  |  | Front |  | 93.24 | 105.4101 | 102.7 | 100.9 | 93.4 | 88 | 86.3 | 86.2 | 80.4 | 77.7
|  |  | Rear (Intake) |  | 91.08 | 109.6699 | 106.7 | 106.6 | 82.2 | 68 | 63.9 | 62.9 | 61.8 | 73.3
|  |  | Roof (solid) |  | 94.93 | 107.6709 | 101.6 | 105.9 | 94.9 | 89.2 | 86.8 | 85.6 | 80.7 | 84
|  |  | (Roof Discharge) | 15.0m | 102.56 | 118.7842 | 114.1 | 116.9 | 94 | 69.5 | 68 | 68.1 | 72.8 | 98.1
|  |  | Exhaust Outlet | 2.5m | 100.68 | 117.7527 | 115.2 | 114 | 99.6 | 94.2 | 89.7 | 88.2 | 84.1 | 80.2
Data Centre B
Plant Number | Plant quantity | Plant Name (Source Data) | Total A-Weighted SWL dBA | Unweighted dB at Octave Band Centre Frequency (Hz)
|  |  |  | Total Unweighted Sound Power Level dB | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
1 | 10 | Fresh Air Intake Louvre non-Gen side (Sound Power Level per m2) | 81.81 | 90.4394 | 86.3 | 83.1 | 81.6 | 83.3 | 74.5 | 76 | 76.4 | 67.4 | 53.5
2 | 10 | Fresh Air Intake Louvre Gen side (Sound Power Level per m2) | 79.46 | 87.956 | 83.7 | 80.6 | 77.9 | 81.6 | 72.8 | 74.2 | 73.3 | 63.8 | 41.7
3 | 124 | Exhaust Fan (Single and 2-storey) | 84.3 | 111.2206 | 105.3 | 102.1 | 105.6 | 104 | 101.2 | 97.5 | 92 | 86.3 | 80.2
4 | 4 | VRF Condensers | 72.97 | 83.0917 |  | 81.5 | 71.5 | 74 | 72 | 67 | 62.5 | 56.5 | 53
5 | 12 | Split Unit condensers | 67.33 | 67.1488 |  | 37.2 | 43.5 | 49.1 | 53.5 | 56.9 | 60.9 | 61.9 | 62
6 | 1 | Toilet Exhaust Fan | 75.25 | 77.4803 |  | 63 | 68 | 69 | 73 | 70 | 69 | 62 | 54
7 | 1 | Admin AHU (Air Inlet) | 55.83 | 68.6595 |  | 58 | 68 | 51 | 52 | 47 | 45 | 44 | 41
8 | 1 | Admin AHU (Air Exhaust) | 88.73 | 89.9632 |  | 73 | 81 | 76 | 84 | 85 | 81 | 80 | 71
9 | 1 | Admin AHU (Breakout) | 54.62 | 74.7613 |  | 65 | 70 | 66 | 67 | 64 | 67 | 54 | 31
10 | 96 | CRAC Condensers | 80.72 | 94.2365 |  |  | 93.8 | 83.3 | 73.6 | 70.5 | 66.6 | 59.4 | 54.4
Plant Number | Plant quanlity | Plant Name (Source Data) |  | Total A-Weighted Sound Power Level dBA | Unweighted dB at Octave Band Centre Frequency (Hz)
[5 empty] | Total Unweighted Sound Power Level dB | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
11 | 23 | Generator 75 dB | LHS | 91.68 | 102.3722 | 95 | 100.9 | 86.6 | 87.3 | 84.2 | 83.6 | 78.1 | 84
|  |  | RHS | 91.68 | 102.3722 | 95 | 100.9 | 86.6 | 87.3 | 84.2 | 83.6 | 78.1 | 84
|  |  | Front | 93.24 | 105.4101 | 102.7 | 100.9 | 93.4 | 88 | 86.3 | 86.2 | 80.4 | 77.7
|  |  | Rear (Intake) | 91.08 | 109.6699 | 106.7 | 106.6 | 82.2 | 68 | 63.9 | 62.9 | 61.8 | 73.3
|  |  | Roof (solid) | 94.93 | 107.6709 | 101.6 | 105.9 | 94.9 | 89.2 | 86.8 | 85.6 | 80.7 | 84
|  |  | (Roof Discharge) | 102.56 | 118.7842 | 114.1 | 116.9 | 94 | 69.5 | 68 | 68.1 | 72.8 | 98.1
|  |  | Exhaust Outlet | 100.68 | 117.7527 | 115.2 | 114 | 99.6 | 94.2 | 89.7 | 88.2 | 84.1 | 80.2

## Louvre Calc
Fresh Air Intake Louvre Gen side (Sound Power Level per m2) | Total Sound Power Level dB | Unweighted dB at Octave Band Centre Frequency (Hz)
|  | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Total Unweighted Sound Power Level per m2 dB | 87.956 | 83.7 | 80.6 | 77.9 | 81.6 | 72.8 | 74.2 | 73.3 | 63.8 | 41.7
LDM Acoustic Module, Q-nis Attenuator (4500mm x 2200mm x 2700 mm) Insertion Loss dB | - | - | 13 | 24 | 44 | 50 | 50 | 50 | 50 | 50
Total Unweighted Sound Power Level per m2 dB with attenuator | 83.8099 | 83.7 | 67.6 | 53.9 | 37.6 | 22.8 | 24.2 | 23.3 | 13.8 | -8.3
Fresh Air Intake Louvre non-Gen side (Sound Power Level per m2) | Total Sound Power Level dB | Unweighted dB at Octave Band Centre Frequency (Hz)
|  | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
Total Unweighted Sound Power Level per m2 dB | 90.4394 | 86.3 | 83.1 | 81.6 | 83.3 | 74.5 | 76 | 76.4 | 67.4 | 53.5
LDM Acoustic Module, Q-nis Attenuator (4500mm x 2800mm x 1600 mm) Insertion Loss dB | - | - | 9 | 17 | 29 | 44 | 50 | 50 | 46 | 33
Total Unweighted Sound Power Level per m2 dB with attenuator | 86.5843 | 86.3 | 74.1 | 64.6 | 54.3 | 30.5 | 26 | 26.4 | 21.4 | 20.5

## Exhaust Fan Calc
Exhaust Fan Overall | Total Sound Power Level dB | Unweighted dB at Octave Band Centre Frequency (Hz) | [8 empty] | Exhaust Fan Unit Dimensions
|  | 31.5 | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Side | Area m2 | Total Area m2 | Area correction
Total Unweighted Sound Power Level dB | 111.2206 | 105.3 | 102.1 | 105.6 | 104 | 101.2 | 97.5 | 92 | 86.3 | 80.2 | Short Side | 10 | 71.45 | 18.54
Total Unweighted Sound Power Level dB per unit area | 92.6805 | 86.76 | 83.56 | 87.06 | 85.46 | 82.66 | 78.96 | 73.46 | 67.76 | 61.66 | Long Side | 19.6
Danaan Air DH Extract Unit 1200 mm with fan flow grids Insertion Loss dB | - | - | 8 | 13 | 22 | 36 | 45 | 45 | 36 | 24 | Roof | 12.25
Total Unweighted Sound Power Level dB per unit area with attenuator | 87.3428 | 86.8 | 75.56 | 74.06 | 63.46 | 46.66 | 33.96 | 28.46 | 31.76 | 37.66

## AHU Calc
AHU Breakout Overall | Total Sound Power Level dB | Unweighted dB at Octave Band Centre Frequency (Hz) | [7 empty] | AHU Unit Dimensions
|  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Side | Area m2 | Total Area m2 | Area correction
Total Unweighted Sound Power Level dB | 74.7613 | 65 | 70 | 66 | 67 | 64 | 67 | 54 | 31 | Short Side | 5.76 | 43.92 | 16.4266
Total Unweighted Sound Power Level dB per unit area | 58.3347 | 48.5734 | 53.5734 | 49.5734 | 50.5734 | 47.5734 | 50.5734 | 37.5734 | 14.5734 | Long Side | 10.8
[10 empty] | Roof | 10.8