## Summary
Modelling Results Summary
Modelling Scenario | Noise Sensitive receptors | Predicted Noise Levels |  | Noise Limits |  | Difference between predicted noise levels and noise limits
|  | Day/night LAeq dB |  | Day/night LA90 dB
|  | Daytime | Night-time | Daytime | Night-time | Daytime | Night-time
Generator maintenance | R1 | 34 | - | 41.4957 | - | -7.4957 | -
| R2 | 42 | - | 42.4305 | - | -0.43049 | -
| R3 | 39 | - | 43.9667 | - | -4.9667 | -
| R4 | 35 | - | 45.5667 | - | -10.5667 | -
Emergency generator operation | R1 | 47.1 | 47.1 | 41.4957 | 36.9112 | 5.6043 | 10.1888
| R2 | 52 | 52 | 42.4305 | 40.1863 | 9.5695 | 11.8137
| R3 | 53 | 53 | 43.9667 | 43.9 | 9.0333 | 9.1
| R4 | 47 | 47 | 45.5667 | 40.85 | 1.4333 | 6.15