## MCP_or_generator_list
Plant Name | Point Source Emission Reference | NACE Code (required information) | Traceable identifier for the individual medium combustion plant (MCP) or generator (required information) | Plant Manufacturer | Model Name | Is the plant stationary or mobile? | Stack or emission point national grid reference (required information) | Easting | Northing | Latitude | Longitude | Date operation started (required information) | Rated thermal input of the individual MCP or generator in MW thermal (required information) | Total rated thermal input of all plant or generators on site in MWth | Technology or type (required information) | Main fuel type used (required information) | Secondary fuel type used (required information if plant is dual fired or uses a secondary fuel as a back up) | Is the secondary fuel used as a back up? and/or does the plant co fire using the secondary fuel? | Percentage of secondary fuel type used | Will the medium combustion plant be operated as a limited operting hours plant? (required information) | Annual operating hours. Please enter the hours the plant is intended to run. | Do you want to declare that your existing MCP will meet new MCP emission limit values (ELVs) from the medium combustion plant directive? | Annual load factor as a percentage | Background nitrogen dioxide (NO2) in ug/m3 | Stack height (meters) | What is the emission rate for the pollutants (Nm3/s ) | Is the plant in an Air Quality Management Area (AQMA) for a declared pollutant? | What is the name of the local authority who has declared th AQMA? | Closest human receptor (meters) | Human receptor details | Closest Ecological receptor (meters) | Ecological receptor details | Will secondary abatement be fitted to the plant | What type of secondary abatement will be fitted? | date of capacity market of balancing service agreement or FiT accreditation (DD/MM/YYYY)
Guidance | See 2324033 – ERA Figure 3 Emission Points to Atmosphere – Generator Stacks | NACE code means Nomenclature of Economic Activities and is the European statistical classification of economic activities | Serial number or other unique identifier, name plate, manufacturer and or model | Indicative Manufacture only - Suppier not yet selected. |  |  | Enter the coordinates of the emission point of the plant (not the site). You should enter this as a National Grid Reference or as a Latitude and Longitude pair. You should enter the values using the same coordinate system that you collected the raw data in. |  |  |  |  | When the plant or generator was first put into operation or the commissioning date, leave blank if new and not yet operating | This is for each individual unit. You should calculate this using one of the methods given in this guidance on calculating capacity: | This should be the total of all the individual units of any size | Boiler, Engine, Back up generator, turbine, boiler CHP, Engine CHP | Gas oil, Gas oil substitute, Hydrogen, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels | Gas oil, Gas oil substitute, Hydrogen, Liquid fuels other than gas oil, Natural gas, Biogas, Other gaseous fuels, Solid biomass, Waste biomass, Woody solid biomass, Straw, Other solid fuels | Back up, co firing, both | Only required where co firing | Where the option of exemption under Article 6 (8) of the medium combustion plant directive is used the operator (as identified in Part A of the application form) can declare by indicating here that the MCP will not be operated more than the number of hours referred to in this paragraph. | This should be the total for the year and be to the nearest whole number | Applicable for existing MCP plant only. You may want to claim this to demonstrate low risk impacts to habitats as part of an air emissions risk assessment. If you do make this voluntary declaration we will include new MCP ELVs from the medium combustion plant directive in your permit. |  | Go to the Defra UK Air website and select the most recent background map data. Set the local authority to that of your site location and the pollutant to NO2 |  |  | AQMAs interactive map | [7 empty] | applicable to SG applications only
|  | Full Classification | [10 empty] | Capacity Guidance | [10 empty] | Background Mapping data for local authorities - Defra, UK
|  | Simple List | [13 empty] | Click Here to see MCP New Fuels Direction 2024
Emergency Standby Generator (Back up 1) | A1 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503348.3 | 180454 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil |  |  |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Emergency Standby Generator (Back up 2) | A2 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503354.3 | 180455.8 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing | HVO Gas oil substitute will be used subject to availability | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 1 | A3 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503360.3 | 180457.6 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 2 | A4 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503366.4 | 180459.4 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 3 | A5 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503372.4 | 180461.2 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 4 | A6 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503378.4 | 180463 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 5 | A7 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503384.4 | 180464.9 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 6 | A8 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503390.4 | 180466.7 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 7 | A9 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503396.5 | 180468.5 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 8 | A10 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503402.5 | 180470.3 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 9 | A11 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503408.5 | 180472.1 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 10 | A12 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503414.5 | 180474 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 11 | A13 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503420.6 | 180475.8 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 12 | A14 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503426.6 | 180477.6 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 13 | A15 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503432.6 | 180479.4 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 14 | A16 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503438.7 | 180481.3 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 15 | A17 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503444.7 | 180483.1 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 16 | A18 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503450.7 | 180484.9 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 17 | A19 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503456.7 | 180486.7 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 18 | A20 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503462.7 | 180488.5 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 19 | A21 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503468.7 | 180490.3 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 20 | A22 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503474.8 | 180492.2 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 21 | A23 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503480.8 | 180494 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 22 | A24 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503486.8 | 180495.8 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 23 | A25 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503492.8 | 180497.6 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
Standby Generator 24 | A26 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503498.9 | 180499.4 |  |  |  | 8.48 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 9.15 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
House Generator | A27 | J63 | N/A - MCP not yet purchased | CAT | Not yet selected | Stationary |  | 503500.9 | 180500.1 |  |  |  | 2.5 | 222.98 | Back up generator | Gas oil | Gas oil substitute | Co firing |  | Yes | 500 |  | 100 | 20.4 | 25 | 2.32 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No
222.98
Add more rows as you need them

## Thermal Input Rating Calc
| Deployment | Critical
Model | Reference Model | CAT C175-20 EM1365
Fuel | 824.7 | at 100% Power Rating
Diesel | 42700 | Calorific Value (LHV)
Density | 0.85 | Fuel Density
Thermal Input | 8314.5796 | Thermal Input ["=Consumption (l/hr) x calorific value x density"]
| 8480.8712 | added 2% margin for BImSchG application
| Deployment | House
| Reference Model | CAT C32 EM0777
| 252.3 | at 100% Power Rating
| 42700 | Calorific Value (LHV)
| 0.85 | Fuel Density
| 2543.6746 | Thermal Input ["=Consumption (l/hr) x calorific value x density"]
| 2594.5481 | added 2% margin for BImSchG application

## Resp_1 (hidden)
Plant Name | _1136 | _1333 | _1234 | Easting | Northing | Lat | Long | _1224 | _1137 | _1118 | _1125 | _1152 | _1230 | _1138 | _1328 | _1062 | _1326 | _1021 | _1015 | _1140 | _1121 | _1117 | _1124 | _2005 | _1016 | _2006 | _1150 | _1040 | _1225 | _2017 | Release Point NGR | Mobile Plant | NACE Code
Emergency Standby Generator (Back up 1) | Not yet selected | CAT | #REF! | 503348.3 | 180454 | 0 | 0 | 0 | 8.48 | Back up generator | #REF! | 0 | 0 | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Emergency Standby Generator (Back up 2) | Not yet selected | CAT | #REF! | 503354.3 | 180455.8 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | HVO Gas oil substitute will be used subject to availability | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 1 | Not yet selected | CAT | #REF! | 503360.3 | #REF! | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 2 | Not yet selected | CAT | #REF! | 180457.6 | 180459.4 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 3 | Not yet selected | CAT | #REF! | 503372.4 | 180461.2 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 4 | Not yet selected | CAT | #REF! | 503378.4 | 180463 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 5 | Not yet selected | CAT | #REF! | 503384.4 | 180464.9 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 6 | Not yet selected | CAT | #REF! | 503390.4 | 180466.7 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 7 | Not yet selected | CAT | #REF! | 503396.5 | 180468.5 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
Standby Generator 8 | Not yet selected | CAT | #REF! | 503402.5 | 180470.3 | 0 | 0 | 0 | 8.48 | Back up generator | Gas oil | Gas oil substitute | Co firing | 0 | Yes | 500 | 0 | 100 | 20.4 | 25 | Yes | Buckinghamshire Council | 55 | Residential | 3830 | Black Park SSSI | No | 0 | 0 | 9.15 | 0 | No | J63
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0
Named Range | Value | [6 empty] | MCP-DateCommissioned | ThermalInput | MCP-CombustionTechnology | MCP-FuelMain | MCP-FuelSec | MCP-FuelSecWhen | MCP-FuelUsageSec | MCP-Limitedhrs |  | MeetnewELV | MCP-Loadas% | MCP-BackgroundNO2 | MCP-StackHeight | AQMA | AQMA LA | HumanReceptor | MCP_HumanReceptorDetails | EcoReceptor | MCP_EcoReceptorDetails | MCP-Abated | MCP-AbateType | MCP-CapBalAgree
MobilePlant | No
NaceCode | J63
Plant Name | Plant Name
_1136 | Serial No. of Plant (If already purchased)
_1333 | Plant Manufacturer
_1234 | Model Name
Easting | Easting
Northing | Northing
Lat | Lat
Long | Long
_1224 | Commissioning Date
_1137 | Size (MWth)
_1118 | Technology
_1125 | Fuel/Main Fuel
IF an individual plant uses more than one fuel, give the proportions | IF an individual plant uses more than one fuel, give the proportions
0 | 0
02 | 0
03 | 0
04 | 0
Stack Height (metres) | Stack Height (metres)
_1027 | If new plant does the flue share a common windshield?
_1062 | Annual Hours
_1328 | Limited Operating Hours
_1021 | Annual Load (%)
_1121 | In AQMA
_1117 | AQMA Local Authority
_1124 | Closest Human Receptor (metres)
_2005 | Human Receptor Details
_1016 | Closest Ecological Receptor (metres)
_2006 | Ecological Receptor Details
_1015 | Background NO2 (μg/m3)
_1150 | Will secondary abatement be fitted to the plant?
_1040 | Abatement Type
_1326 | Will Meet New ELVs