## MCP Generator Info
Data Centre Virtus LON4, LON3, LON10 |  |  | Emission Point Grid Ref |  |  | Generator Info
Data Centre | Emission Point Ref | MCP Specific Identifier: Serial # | X | Y | Z (m) | Engine Type: Diesel | Fuel | X | Y | Tech Spec data sheet | Thermal Input default method MWth | Thermal input based on fuel consumption MWth | Order date | Commissioning Date | NACE | Expected Operating Hours | Article 6(3) or 6(8) exemption | Company Name | Registered Office
LON4 | A1 | 528 104 491 | 495801.728 | 181358.7873 | 10.1 | AVK XC3300,G63 TAL (MTU) | Gas Oil 100% | 495810 | 181353 | L4 EDS40000451-1-0002-EMISSIONSDATENBLATT-C | 6.86 | 7.28 | pre-2018 | 2013 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A2 | 528 103 521 | 495804.5855 | 181352.9135 | 10.1 | AVK XC3300,G63 TAL (MTU) | Gas Oil 100% | 495813 | 181346 | L4 EDS40000451-1-0002-EMISSIONSDATENBLATT-C | 6.86 | 7.28 | pre-2018 | 2013 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A3 | 528 102 912 | 495802.998 | 181347.8335 | 10.1 | AVK XC3300,G63 TAL (MTU) | Gas Oil 100% | 495811 | 181341 | L4 EDS40000451-1-0002-EMISSIONSDATENBLATT-C | 6.86 | 7.28 | pre-2018 | 2013 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A4 | 528 102 911 | 495801.4105 | 181342.9122 | 10.1 | AVK XC3300,G63 TAL (MTU) | Gas Oil 100% | 495810 | 181335 | L4 EDS40000451-1-0002-EMISSIONSDATENBLATT-C | 6.86 | 7.28 | pre-2018 | 2016-04-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A5 | 528 102 900 | 495799.9818 | 181337.8322 | 10.1 | AVK XC3300,G63 TAL (MTU) | Gas Oil 100% | 495808 | 181330 | L4 EDS40000451-1-0002-EMISSIONSDATENBLATT-C | 6.86 | 7.28 | pre-2018 | 2018-08-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A6 | SBK02114 | 495798.7118 | 181333.0697 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495807 | 181325 | L4 TMI 2750kVA 3516C HD low ems EM2883.pdf | 6.29 | 6.04 | 2016-06-29 | 2016-12-16 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A7 | SBK02180 | 495797.4418 | 181328.4659 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495805 | 181320 | L4 TMI 2750kVA 3516C HD low ems EM2883.pdf | 6.29 | 6.04 | 2016-06-29 | 2017-03-21 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A8 | SBK02179 | 495796.1718 | 181324.0209 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495804 | 181316 | L4 TMI 2750kVA 3516C HD low ems EM2883.pdf | 6.29 | 6.04 | 2016-06-29 | 2017-03-27 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A9 | SNF00167 | 495795.2193 | 181320.6872 | 10.1 | CAT 3516B | Gas Oil 100% | 495802 | 181312 | L4 3516B TMI 2500kVA EO 60C SCAC and L4 3516B TMI 2500kVA EO 90C SCAC interpolated | 5.71 | 5.61 | 2021-02-05 | TBC | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A10 | SNF00169 | 495794.108 | 181316.8772 | 10.1 | CAT 3516B | Gas Oil 100% | 495801 | 181308 | L4 3516B TMI 2500kVA EO 60C SCAC and L4 3516B TMI 2500kVA EO 90C SCAC interpolated | 5.71 | 5.61 | 2021-02-05 | TBC | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A11 | SNF00168 | 495792.838 | 181312.9084 | 10.1 | CAT 3516B | Gas Oil 100% | 495800 | 181304 | L4 3516B TMI 2500kVA EO 60C SCAC and L4 3516B TMI 2500kVA EO 90C SCAC interpolated | 5.71 | 5.61 | 2021-02-05 | TBC | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A12 | SBK02536 | 495792.3618 | 181309.2572 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495799 | 181299 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2017-04-19 | 2018-01-04 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A13 | SBK02535 | 495790.933 | 181305.4472 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495798 | 181295 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2017-04-19 | 2017-12-05 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A14 | SBK02534 | 495790.1393 | 181301.6371 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495797 | 181292 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2017-04-19 | 2017-12-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A15 | SBK02533 | 495789.028 | 181297.9859 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495796 | 181288 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2017-04-19 | 2017-12-21 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A16 | SBK20793 | 495787.4405 | 181293.0646 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495794 | 181282 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2017-05-17 | 2018-10-19 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A17 | LYM00164 | 495786.6468 | 181287.9846 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495792 | 181277 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2018-05-17 | 2019-05-23 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A18 | LYM00166 | 495790.298 | 181287.3496 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495795 | 181276 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2018-05-17 | 2019-05-14 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON4 | A19 | LYM02444 | 495785.6943 | 181284.3334 | 10.1 | CAT 3516C - HD | Gas Oil 100% | 495790 | 181273 | L4 3516C TMI Standby 2200kWe EM0599.pdf (or use the remap version above… EM2883) | 6.29 | 6.04 | 2021-02-05 | TBC | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A21 | 546 100 176 | 495711.9081 | 181263.7603 | 14.85 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495705 | 181264 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A22 | 546 100 178 | 495710.531 | 181259.0273 | 15.725 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495704 | 181260 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A23 | 548 100 300 | 495709.4239 | 181255.0328 | 16.231 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495702 | 181256 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A24 | 548 100 301 | 495707.9769 | 181250.1555 | 16.25 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495701 | 181251 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A25 | 548 100 177 | 495706.8828 | 181246.3291 | 15.725 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495699 | 181247 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON3 | A26 | 548 100 175 | 495705.4461 | 181241.5502 | 14.65 | AVK DS2500 (MTU 4000G63) | Gas Oil 100% | 495698 | 181243 | L3 ZNG00013253_EMISSIONSDATENBLATT | 5.14 | 4.72 | 2018-06-01 | 2019-01-01 | 62.09 | <50 | N/A | Virtus Slough Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A27 | 548 100 789 | 495789.7444 | 181197.9558 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495798 | 181193 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A28 | 548 100 791 | 495788.6596 | 181193.8548 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495796 | 181189 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A29 | 548 100 790 | 495787.4954 | 181189.7537 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495795 | 181185 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A30 | 548 100 788 | 495786.3048 | 181185.8643 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495793 | 181181 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A31 | 548 100 784 | 495785.0613 | 181181.8956 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495792 | 181176 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON10 | A32 | tbc not yet installed | 495783.8706 | 181177.9268 | 15.98 | AVK DS2500 (MTU 4000G84F) | Gas Oil 100% | 495791 | 181172 | L10 ZNG00013256_EMISSIONSDATENBLATT | 5.14 | 5.42 | Post 2018 | 2021 | 62.09 | <50 | N/A | Virtus London 10 Limited | 4th Floor 20 Balderton Street, London, England, W1K 6TL
LON12 | A33 | tbc not yet installed | 495825 | 181194 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A34 | tbc not yet installed | 495828 | 181193 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A35 | tbc not yet installed | 495824 | 181190 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A36 | tbc not yet installed | 495827 | 181189 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A37 | tbc not yet installed | 495823 | 181186 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A38 | tbc not yet installed | 495826 | 181185 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A39 | tbc not yet installed | 495870 | 181215 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A40 | tbc not yet installed | 495874 | 181213 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A41 | tbc not yet installed | 495868 | 181212 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A42 | tbc not yet installed | 495873 | 181210 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A43 | tbc not yet installed | 495867 | 181208 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A44 | tbc not yet installed | 495872 | 181205 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A45 | tbc not yet installed | 495866 | 181204 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A46 | tbc not yet installed | 495870 | 181201 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A47 | tbc not yet installed | 495865 | 181198 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
LON12 | A48 | tbc not yet installed | 495869 | 181195 | 23 | MTU DS3100 G74F emissions optimised (EO). | Gas Oil 100% |  |  | Appendix D of the Supporting Informaiton Document | 7.06 | 6.34 |  | 2025-08-01 | 62.09 | <50 | N/A | Virus HoldCo Ltd | 4th Floor, 20 Balderton Street, London, England, W1K 6TL
[10 empty] | TOTAL | 295.26 | 281.95