## STORAGE LOCATIONS
PLAN REF | DRAWING | WASTE STORED | TRANSFER STATION / PLASTICS / LOWER YARD | FORM | READILY COMBUSTIBLE | CONTAINS POPS? | MAX STORAGE TIME | MAX LENGTH (M) | MAX WIDTH (M) | MAX HEIGHT OF WASTE STORED (M) | SURFACE AREA (M2) | VOL OF WASTE STORED PER BAY (M3) | VOLUME OF WATER NEEDED TO FIGHT FIRE BASED ON PILE SIZE (M3) | VOLUME OF CONTAINMENT NEEDED TO CONTAIN FIRE WATER & WASTE STORED IN BAY IF LIQUIDS (M3) | CAPACITY WITHIN SECONDARY CONTAINMENT (M3) | CONTAINMENT CAPACITY WITHIN TERTIARY CONTAINMENT AREA (M3) | CONTAINMENT TYPE | FIREWATER CONTAINMENT | STOCK ROTATION
A10 | BKP-FPP-V08 -01 -Upper Yard | RECEPTION AREA (ASSUMING FILLED WITH COMBUSTIBLE WASTES) | TRANSFER STATION | UNPROCESSED | YES | YES | 24 HOURS | 10 | 4 | 1.2 | 40 | 30 | 36 | 76 | 4 | 205 | WITHIN EXISTING BUILDING WITH PRECAST CONCRETE WALLS ON EITHER SIDE, IMPERMEABLE CONCRETE FLOOR | CONTAINMENT WITHIN OUTER BUNDED IMPERMEABLE SURFACE IF LOCAL BUNDING BREACHED. DRAINAGE FALLS TO MAIN YARD DRAIMAGE SYSTEM AND 500MM HIGH TERTIARY CONTAINMENT ADJACENT TO ROLLER BUND | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE CHECKED BY A MINIMUM HNC QUALIFIED CHEMIST WITHIN 24 HOURS OF RECIEPT AND THEN PLACED IN APPROPRIATE BAYS AS PER HSG71
C31 | BKP-FPP-V5-01 Lower Yard | LITHIUM METAL BATTERIES (PRIMARY) | LOWER YARD | SORTED / UNSORTED MIXED BATTERIES | YES | YES | 3 MONTHS | 4 | 2 | 2.4 | 8 | 8 | 9.6 | 9.6 |  | >250 | SELF-BUNDED METAL CONTAINER WITH >1,100L CONTAINMENT. BATTERIES STORED IN DRUMS WITH INERT PACKING MATERIAL. CONTAINER ON CONCRETE IMPERMEABLE SURFACE SURROUNDED BY FIRE RATED BLOCKS |  | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
C31A | BKP-FPP-V5-01 Lower Yard | LITHIUM LION BATTERIES (SECONDARY) | LOWER YARD | SORTED / UNSORTED MIXED BATTERIES | YES | YES | 3 MONTHS | 4 | 2 | 2.4 | 8 | 8 | 9.6 | 9.6 |  | >250 | SELF-BUNDED METAL CONTAINER WITH >1,100L CONTAINMENT. BATTERIES STORED IN DRUMS WITH INERT PACKING MATERIAL. CONTAINER ON CONCRETE IMPERMEABLE SURFACE SURROUNDED BY FIRE RATED BLOCKS |  | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
A11 | BKP-FPP-V08 -01 -Upper Yard | OXIDISERS | TRANSFER STATION | UNPROCESSED | YES | NO | 6 MONTHS | 4 | 2 | 2.4 | 8 | 8 | 9.6 | 17.6 | 4 | 205 | BUNDED PALLETS. INSIDE SMALLER BUNDED AREA OF 39.1M BEFORE BREACHING INTO OUTER TERTIARY CONTAINMENT AREA | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA, INSIDE SMALLER BUNDED AREA OF 39.1M BEFORE BREACHING INTO OUTER CONTAINMENT AREA OF 108.5m3 (INCLUDING OFFLOADING TANK) | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A2 | BKP-FPP-V08 -01 -Upper Yard | TOXIC | TRANSFER STATION | UNPROCESSED | NO | NO | 6 MONTHS | 4 | 6 | 2.4 | 24 | 20 |  |  | 4 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA of 108.5M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A3 | BKP-FPP-V08 -01 -Upper Yard | FLAM SOLID | TRANSFER STATION | UNPROCESSED | YES | NO | 6 MONTHS | 13 | 4.6 | 2.4 | 59.8 | 40 | 48 | 48 | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS. OUTER BUNDED AREA HAS 108.5M3 CAPACITY | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA OF >108.5M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A4 | BKP-FPP-V08 -01 -Upper Yard | ALKALI | TRANSFER STATION | UNPROCESSED | NO | NO | 6 MONTHS | 10.5 | 4.6 | 2.4 | 48.3 | 40 |  |  | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
A5 | BKP-FPP-V08 -01 -Upper Yard | WEEE | TRANSFER STATION | UNPROCESSED | NO | YES | 6 MONTHS | 10.5 | 4.6 | 2.4 | 48.3 | 40 | 48 | 48 | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING CIRIA 736 / BAT / EA FPP GUIDANCE | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A6 | BKP-FPP-V08 -01 -Upper Yard | ACIDIC | TRANSFER STATION | UNPROCESSED | NO | NO | 6 MONTHS | 10.5 | 4.6 | 2.4 | 48.3 | 40 |  |  | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A7 | BKP-FPP-V08 -01 -Upper Yard | NON/LOW HAZ | TRANSFER STATION | UNPROCESSED | NO | NO | 6 MONTHS | 10.5 | 4.6 | 2.4 | 48.3 | 40 |  |  | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
A8 | BKP-FPP-V08 -01 -Upper Yard | FLAMMABLE LIQUIDS | TRANSFER STATION | UNPROCESSED | YES | NO | 6 MONTHS | 10.5 | 4 | 2.4 | 42 | 30 | 36 | 66 | 6 | 205 | SELF BUNDED CONCRETE BAY WITH SELF CONTAINED DRAINAGE, MEETING BAT / HSG71 STANDARDS. OUTER BUNDED AREA HAS 108.5M3 CAPACITY | CONTAINMENT WITHIN SELF BUNDED AREA INITIALLY. CONTAINER IS CONTAINED WITHIN LARGER BUNDED AREA OF >108.5M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
B14 | BKP-FPP-V08 -01 -Upper Yard | UNWASHED METALLIC CONTAINERS TO BE LAUNDERED AND RECYCLED | PLASTICS | UNPROCESSED | NO | NO | 3 MONTHS | 10 | 2 | 3.6 | 20 | 30 |  |  | 204 |  | STORED WITHIN NEW BUNDED AREA. METALLIC CONTAINERS SEGREGATED FROM COMBUSTIBLE CONTAINERS IN ROWS | CONTAINMENT WITHIN BUNDED AREA OF >249M3 CAPACITY | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
A13 | BKP-FPP-V08 -01 -Upper Yard | AEROSOLS | TRANSFER STATION | UNPROCESSED | YES | NO | 3 MONTHS | 5.9 | 2.3 | 2.4 | 13.57 | 12 | 14.4 | 14.4 |  | 205 | STORED IN VENTED DRUMS OR WASTESAFES ON MAIN YARD IN DRUMS INSIDE A VENTILATED 20FT SHIPPING CONTAINER CAGE COMPLIANT WITH HSG51 AND GUIDANCE FOR STORAGE AND TREATMENT OF AEROSOLS CANISTERS AND SIMILAR PACKAGED WASTES. CONTAINER IS SURROUNDED BY LEGO BLOCK FIRE WALL ON LOWER SIDE. AREA MONITORED FOR VOC AND ONLY INTRINSICALLY SAFE EQUIPNENT USED IN THIS AREA | CONTAINMENT WITHIN SHIPPING CONTAINER. FIRE WATER WOULD BE ISOLATED WITHIN FIRST DRAINAGE AREA AND CHANNEL ALONG RETAINING WALL AND WOULD NOT BE ABLE TO SPREAD TO OTHER AREAS OF THE SITE. FIRE WALLA SURROUND 3 SIDES OF CONTAINER. ENTRANCE POINTING TOWARDS UNUSED AREA OF SITE | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
A12 | BKP-FPP-V08 -01 -Upper Yard | GAS CYLINDERS | TRANSFER STATION | UNPROCESSED | YES | NO | 3 MONTHS | 3 | 3 | 2 | 9 | 2 | 2.4 | 2.4 |  | 205 | STORED IN CAGE SURROUNDED BY FIRE RATED BLOCKS WITHIN A CAGE COMPLIANT WITH HSG51 AND GUIDANCE FOR STORAGE AND TREATMENT OF AEROSOLS AND SIMILAR PACKAGED WASTES | FIRE WATER WOULD BE ISOLATED WITHIN FIRST DRAINAGE AREA AND CHANNEL ALONG RETAINING WALL AND WOULD NOT BE ABLE TO SPREAD TO OTHER AREAS OF THE SITE. FIRE WALLS ACROSS 3 SIDES | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
B14 | BKP-FPP-V08 -01 -Upper Yard | UNWASHED PLASTIC CONTAINERS | PLASTICS | UNPROCESSED | YES | NO | 3 MONTHS | 8 | 4 | 3.6 | 32 | 90 | 108 | 108 | 204 |  | STORED WITHIN BUNDED AREA WRAPPED ON PALLETS, WITHIN BUND B WITH 70M3 CAPACITY | CONTAINMENT WITHIN BUNDED AREA OF >249M3 CAPACITY | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
C1 | BKP-FPP-V08-01 -Lower Yard Layout | DIESEL TANK | LOWER YARD | NON WASTE | YES | NO | N/A | 6 | 3 | 3 | 18 | 10 | 12 | 22 |  | >250 | SELF BUNDED FUEL TANK ONTOP OF CONCRETE PLINTH, STORED WITHIN OUTER BUNDED IMPERMEABLE SURFACE THAT HAS >200M3 CAPACITY | CONTAINMENT WITHIN SELF-BUNDED TANK AND THEN LARGER BUNDED SITE OF >200M3 | FUEL IS PERIODICALLY REFILLED WHEN LEVELS ARE REDUCED FROM REFILLING SITE VEHICLES / HGVS
C4 | BKP-FPP-V08-01 -Lower Yard Layout | RECEPTION AREA | LOWER YARD | UNPROCESSED | YES | NO | 24 HOURS | 10 | 5 | 1.2 | 50 | 24 | 28.8 | 52.8 | 4 | >250 | CONCRETE BAY WITH STEEL WALLED BAY WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | CONTAINMENT WITHIN LARGER BUNDED AREA OF >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE CHECKED BY A MINIMUM HNC QUALIFIED CHEMIST WITHIN 24 HOURS OF RECIEPT AND THEN PLACED IN APPROPRIATE BAYS AS PER HGS71
C6 | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED ANTIFREEZE / OIL AND WATER STORAGE | LOWER YARD | UNPROCESSED | NO | NO | 6 MONTHS | 12 | 5 | 2.4 | 60 | 48 |  |  | 4 | >250 | CONCRETE BAY WITH STEEL WALLED BAY WITHIN BUNDED AREA | CONTAINMENT WITHIN SELF-BUNDED TANK AND THEN LARGER BUNDED SITE | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
D20 | BKP-FPP-V08-01 -Lower Yard Layout | oAVC | LOWER YARD | PROCESSED | YES | NO | 1 MONTH | 6 | 2.4 | 2.7 | 14.4 | 20 | 24 | 44 | 176 | >250 | WITHIN BUND WHICH IS WITHIN BUNDED AREA, BUND HAS 108M3 CAPACITY, BUND IS WITHIN OUTER BUND THAT HAS >200M3 CAPACITY | BUNDED AREA HAS CONTAINMENT OF 100M3, THEN BUND IS WITHIN LARGER BUNDED AREA OF >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
C22 | BKP-FPP-V08-01 -Lower Yard Layout | FILTER PRESS | LOWER YARD | PROCESSED | NO | NO | 1 DAY | 4 | 1 | N/A | 4 | 0.8 |  |  | 5 | >250 | WITHIN BUND WHICH IS WITHIN BUNDED AREA | BUNDED AREA HAS CONTAINMENT, THEN BUND IS WITHIN LARGER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
C25 | BKP-FPP-V08-01 -Lower Yard Layout | GENERAL WASTE SKIP | LOWER YARD | PROCESSED | YES | NO | 5 DAYS | 6 | 2.4 | 2.7 | 14.4 | 30.6 | 36.72 | 36.72 |  | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
C26 | BKP-FPP-V08-01 -Lower Yard Layout | WOOD SKIP (PALLETS) | LOWER YARD | PROCESSED | YES | NO | 5 DAYS | 6 | 2.4 | 2.7 | 14.4 | 30.6 | 36.72 | 36.72 |  | >250
C27 | BKP-FPP-V08-01 -Lower Yard Layout | QUARANTINE AREA | LOWER YARD | NON WASTE | N/A |  | N/A | 10 | 7 | 2.7 | 70 | 30.6 | 36.72 | 36.72 |  | >250 | WITHIN BUNDED AREA | BUNDED IMPERMEABLE SURFACE | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
C34 | BKP-FPP-V08-01 -Lower Yard Layout | GAC SILO FOR SURFACE WATER POLISHING | LOWER YARD | NON WASTE | NO - SUBMERGED IN WATER | NO | 6 MONTHS | 2 | 2 | 3 |  |  | 0 |  | 108
C34A | BKP-FPP-V08-01 -Lower Yard Layout | GAC SILO FOR SURFACE WATER POLISHING | LOWER YARD | NON WASTE | NO - SUBMERGED IN WATER | NO | 6 MONTHS | 2 | 2 | 3 |  |  | 0 |  | 108
D7 | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED OIL AND WATER | LOWER YARD | UNPROCESSED | NO |  | 6 MONTHS | 6 | 8 | 2.4 | 48 | 48 |  |  | 6 |  | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
D8 | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED OILY RAGS / ABSORBENTS | LOWER YARD | UNPROCESSED | YES |  | 3 MONTHS | 12.9 | 2.6 | 2.4 | 33.54 | 24 | 28.8 | 28.8 |  | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
D8A | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED OILY RAGS / ABSORBENTS | LOWER YARD | UNPROCESSED | YES |  | 3 MONTHS | 12.9 | 2.6 | 2.4 | 33.54 | 24 | 28.8 | 28.8 |  | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
D8B | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED OILY RAGS / ABSORBENTS | LOWER YARD | UNPROCESSED | YES |  | 3 MONTHS | 12.9 | 2.6 | 2.4 | 33.54 | 24 | 28.8 | 28.8 |  | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE MAXIMUM STORAGE TIME ON SITE WILL BE 3 MONTHS
D10 | BKP-FPP-V08-01 -Lower Yard Layout | EMPTY CONTAINER STORAGE | LOWER YARD | PROCESSED | NO |  | 6 MONTHS | 8 | 7 | 2.4 | 56 | 70 | 84 | 84 |  | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
D9 | BKP-FPP-V08-01 -Lower Yard Layout | OILY ABSORBENTS / REPACKED | LOWER YARD | PROCESSED | NO |  | 24 HOURS | 7 | 6 | 2.4 | 42 | 50 | 60 | 60 | 6 | >250 | WITHIN BUNDED AREA THAT HAS >200M3 CAPACITY. SELF-CONTAINED DRAINAGE WITHIN OTHER BUNDED AREA. SURROUNDED BY 4 HIGH 600MM THICK CONCRETE FIRE RATED BLOCKS | BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T1 | BKP-FPP-V08-01 -Lower Yard Layout | WASTE OIL | LOWER YARD | UNPROCESSED | YES |  | 6 MONTHS | 3 | 3 | 9 | 9 | 62 | 74.4 | 136.2 | 176 | >250 | METAL TANK WITHIN BUND THAT IS DESIGNED & CONSTRUCTED IN ACCORDANCE WITH CIRIA 736 | BUND HAS 176,000L CAPACITY. BUND IS WITHIN BUNDED AREA OF >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T2 | BKP-FPP-V08-01 -Lower Yard Layout | WASTE OIL | LOWER YARD | UNPROCESSED | YES |  | 6 MONTHS | 3 | 3 | 9 | 9 | 62 | 74.4 | 136.2 | 176 | >250 | METAL TANK WITHIN BUND THAT IS DESIGNED & CONSTRUCTED IN ACCORDANCE WITH CIRIA 736 | BUND HAS 176,000L CAPACITY. BUND IS WITHIN BUNDED AREA >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T3 | BKP-FPP-V08-01 -Lower Yard Layout | SOLUBLE OIL | LOWER YARD | PROCESSED | NO |  | 6 MONTHS | 3 | 3 | 9 | 9 | 62 |  |  | 176 | >250 | METAL TANK WITHIN BUND THAT IS DESIGNED & CONSTRUCTED IN ACCORDANCE WITH CIRIA 736 | BUND HAS 176,000L CAPACITY. BUND IS WITHIN BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T4 | BKP-FPP-V08-01 -Lower Yard Layout | WASTE WATER | LOWER YARD | PROCESSED | NO |  | 6 MONTHS | 3 | 3 | 9 | 9 | 62 |  |  | 176 | >250 | METAL TANK WITHIN BUND THAT IS DESIGNED & CONSTRUCTED IN ACCORDANCE WITH CIRIA 736 | BUND HAS 176,000L CAPACITY. BUND IS WITHIN BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T5 | BKP-FPP-V08-01 -Lower Yard Layout | SURFACE WATER | LOWER YARD | PROCESSED | NO |  | 6 MONTHS | 3 | 3 | 9 | 9 | 62 |  |  | 176 | >250 | METAL TANK WITHIN BUND THAT IS DESIGNED & CONSTRUCTED IN ACCORDANCE WITH CIRIA 736 | BUND HAS 176,000L CAPACITY. BUND IS WITHIN BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T6 | BKP-FPP-V08-01 -Lower Yard Layout | FILTRATE STORAGE FROM SURFACE WATER FILTRATION | LOWER YARD | PROCESSED | NO |  | 6 MONTHS | 3 | 3 | 7 | 9 | 40 |  |  | 46 | >250 | PLASTIC SELF-BUNDED TANK | BUND HAS >100% CAPACITY OF LARGEST VESSEL WITHIN IT. BUND IS WITHIN OUTER BUNDED AREA | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHALL BE REMOVED FROM SITE AS SOON AS POSSIBLE, TYPICALLY WITHIN 1 MONTH. WASTE SHOULD NOT NORMALLY REMAIN ONSITE FOR MORE THAN 3 MONTHS, AND THE MAXIMUM STORAGE TIME WILL BE 6 MONTHS
T7 | BKP-FPP-V08-01 -Lower Yard Layout | SELF-BUNDED SURFACE WATER STORAGE | LOWER YARD | UNPROCESSED | NO |  | 1 WEEK |  |  |  |  | 30 |  |  | 35 | >250 | METAL SELF-BUNDED TANK
T8 | BKP-FPP-V08-01 -Lower Yard Layout | TREATED SURFACE WATER SELF-BUNDED HOLDING TANK | LOWER YARD | PROCESSED | NO |  | 1 WEEK |  |  |  |  | 70 |  |  | 80 | >250 | METAL SELF-BUNDED TANK
D12 | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED NDW |  | UNPROCESSED | YES |  | 1 WEEK | 8 | 6 | 2 | 48 | 48 | 57.6 | 105.6 | 22 | >250 | WITHIN DESIGNATED AREA DESIGNED INLINE WITH CIRIA736 WITHIN LARGER BUNDED AREA. PREVIOUSLY TANKER WASHOUT BAYS THAT HAVE BEEN REPURPOSED | BUNDED AREA HOLDS 26M3 / BAY BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
D13 | BKP-FPP-V08-01 -Lower Yard Layout | PACKAGED NDW |  | UNPROCESSED | YES |  | 1 WEEK | 8 | 6 | 2 | 48 | 48 | 57.6 | 105.6 | 22 | >250 | WITHIN DESIGNATED AREA DESIGNED INLINE WITH CIRIA736 WITHIN LARGER BUNDED AREA. PREVIOUSLY TANKER WASHOUT BAYS THAT HAVE BEEN REPURPOSED | BUNDED AREA HOLDS 26M3 / BAY BUNDED IMPERMEABLE SURFACE >200M3 | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. WASTE SHOULD NOT REMAIN ONSITE FOR MORE THAN 3 MONTHS
D23 | BKP-FPP-V5-01 Lower Yard | SELF BUNDED SURFACE WATER STORAGE TANK |  | UNPROCESSED | NO |  | 1 MONTH | 6 | 3 | 2.5 | 18 | 20 |  |  | 24 | >250 | SELF BUNDED TANK WITHIN BUNDED AREA | FIRST WITHIN BUND, THEN WITHIN BUNDED IMPERMEABLE SURFACE | DYNAMIC STOCK TRACKING SYSTEM WITH DETAILS RECORDS LOCATION AND ONWARD INTENDED DISPOSAL ROUTES. THE WASTE WILL NOT REMAIN IN THE SELF BUNDED TANK FOR MORE THAN ONE MONTH
D30 | BKP-FPP-V5-01 Lower Yard | ELECTRICS KIOSK |  | NON WASTE | NO |  | N/A | 2 | 1 | N/A | 2 | N/A |  |  |  |  | IN KIOSK | OUTSIDE OF BUNDED AREA | ALL PORTABLE ELECTRICAL APPLIANCES ARE PAT TESTED ANNUALLY. ALL FIXED WIRING IS IN CONFORMITY WITH BRITISH STANDARDS AND FIXED WIRING INSPECTIONS ARE COMPLETED BY APPROVED CONTRACTORS AS PART OF PPM
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0