## Testing Parameters
BAT-AEL | Treatment Type | Determinant | Limits | Units | External Accredited Analysis Frequency | Internal Test Method | LOD (Units same as column E) | Notes / Justifications | Units2 | Internal Testing Frequency | Limit for Internal Pass with 10% margin of error
Indirect | Water Based Liquid Waste | Hydrocarbon Oil Index | 0.5-10 | mg/l | Monthly | Inference from COD/TOC |  | See COD/TOC Limits |  | COD for every Load | N/A
Indirect | Water Based Liquid Waste | Free Cyanide | 0.02-0.1 | mg/l | Monthly | Hach Cuvette LCK319 | 0.01 |  | mg/L | Every Discharge | 0.09 mg/L
Indirect | Water Based Liquid Waste | Absorbable Organically Bound Halogens | 0.2-1 | mg/l | Monthly | Hach Cuvette LCK390 | 0.05 | No Chlorinated bleaching agents used, only rainwater so can be disregarded | mg/L | Monthly | N/A
Indirect | Water Based Liquid Waste | Arsenic | 0.01-0.1 | mg/l | Monthly | Ultracarry CG-II XRF | 0.04 |  | mg/L | Every Discharge | 0.09 mg/L
Indirect | Water Based Liquid Waste | Cadmium | 0.01-0.1 | mg/l | Monthly | Hach Cuvette LCK308 | 0.02 |  | mg/L | Every Discharge | 0.09 mg/L
Indirect | Water Based Liquid Waste | Chromium | 0.01-0.3 | mg/L | Monthly | Ultracarry CG-II XRF | 0.02 |  | mg/L | Every Discharge | 0.27 mg/L
Indirect | Water Based Liquid Waste | Hexavalent Chromium | 0.01-0.1 | mg/L | Monthly | Hach Cuvettes LCS313 | 0.05 |  | mg/L | Every Discharge | 0.09 mg/L
Indirect | Water Based Liquid Waste | Copper | 0.05-0.5 | mg/L | Monthly | Ultracarry CG-II XRF | 0.08 |  | mg/L | Every Discharge | 0.45 mg/L
Indirect | Water Based Liquid Waste | Lead | 0.05-0.1 | mg/l | Monthly | Ultracarry CG-II XRF | 0.09 |  | mg/L | Every Discharge | 0.09 mg/L
Indirect | Water Based Liquid Waste | Nickel | 0.05-1 | mg/l | Monthly | Hach Cuvette LCK537 | 0.05 | Only used when Nickel level above LOD on XRF encountered for reassurance on levels | mg/L | When needed | 0.9 mg/L
Indirect | Water Based Liquid Waste | Nickel | 0.05-1 | mg/l | Monthly | Ultracarry CG-II XRF | 0.1 |  | mg/L | Every Discharge | 0.9 mg/L
Indirect | Water Based Liquid Waste | Manganese | N/A | mg/l | Monthly | Ultracarry CG-II XRF | 0.07 |  | mg/l | Every Discharge | 1 mg/L
Indirect | Water Based Liquid Waste | Mercury | 0.5-10 | ug/l | Monthly | Ultracarry CG-II XRF | 70 | Rain water only. Mercury will be removed by GAC, Never detected across years of results from all monthly testing about LOI on external analysis. If any detected above LOD would be quarantined and not discharged. Only segregated rainwater from non-process areas | ug/l | Every Discharge | LOD of Ultra carry
| Water Based Liquid Waste | Mercury | 0.1-10 | ug/l | Monthly | Test Strips - SenSafe® Boris's Mercury Check | 0.2 |  | ug/l | Every Discharge | 9 ug/l
Indirect | Water Based Liquid Waste | Zinc | 0.1-2 | mg/l | Monthly | Ultracarry CG-II XRF | 0.05 |  | mg/L | Every Discharge | 1.8 mg/L
Direct | Water Based Liquid Waste | Total Organic Carbon | 60-100 | mg/l | Monthly | Hach Cuvette LCK385 | 3 |  | mg/L | Every Discharge | 90 mg/L
Direct | Water Based Liquid Waste | Chemical Oxygen Demand (COD) | 30-300 | mg/L | Monthly | Hach Cuvette LCK1414 | 5 |  | mg/L | Every Discharge | 270 mg/L
Direct | Water Based Liquid Waste | Total suspended solids | 05-60 | mg/l | Monthly | Quantofication of suspended solids | 10 |  | mg/L | Every Discharge | 54 mg/L
Direct | Water Based Liquid Waste | Phenol Index | 0.05-0.3 | mg/L | Monthly | Hach Cuvette LCK345 | 0.05 |  | mg/L | Every Discharge | 0.27 mg/L
Direct | Water Based Liquid Waste | Total Nitrogen | 10-60 | mg/L | Monthly | Laton Total Nitrogen | 5 |  | mg/L | Every Discharge | 54 mg/L
Direct | Water Based Liquid Waste | Total Phosphorus | 1-3 | mg/L | Monthly | Ultracarry CG-II XRF | 0.01 |  | mg/L | Every Discharge | 2.7 mg/L