## Intro text
L 208/38 EN Official Journal of the European Union 17.8.2018
DECISIONS
COMMISSION IMPLEMENTING DECISION (EU) 2018/1147 of 10 August 2018
establishing best available techniques (BAT) conclusions for waste treatment, under Directive 2010/75/EU of the European Parliament and of the Council (notified under document C(2018) 5070)
THE EUROPEAN COMMISSION,
Having regard to the Treaty on the Functioning of the European Union,
Having regard to Directive 2010/75/EU of the European Parliament and of the Council of 24 November 2010 on industrial emissions (integrated pollution prevention and control) (1), and in particular Article 13(5) thereof,
Whereas:
(1) Best available techniques (BAT) conclusions are the reference for setting permit conditions for installations covered by Chapter II of Directive 2010/75/EU and competent authorities should set emission limit values which ensure that, under normal operating conditions, emissions do not exceed the emission levels associated with the best available techniques as laid down in the BAT conclusions.
(2) The forum composed of representatives of Member States, the industries concerned and non-governmental organisations promoting environmental protection, established by Commission Decision of 16 May 2011 (2), provided the Commission on 19 December 2017 with its opinion on the proposed content of the BAT reference document for waste treatment. That opinion is publicly available.
(3) The BAT conclusions set out in the Annex to this Decision are the key element of that BAT reference document. (4) The measures provided for in this Decision are in accordance with the opinion of the Committee established by Article 75(1) of Directive 2010/75/EU,
HAS ADOPTED THIS DECISION:
Article 1
The best available techniques (BAT) conclusions for waste treatment, as set out in the Annex, are adopted.
Article 2
This Decision is addressed to the Member States.
Done at Brussels, 10 August 2018.
For the Commission
Karmenu VELLA
Member of the Commission
(1) OJ L 334, 17.12.2010, p. 17.
(2) Commission Decision of 16 May 2011 establishing a forum for the exchange of information pursuant to Article 13 of Directive 2010/75/EU on industrial emissions (OJ C 146, 17.5.2011, p. 3).

## Annex
17.8.2018 EN Official Journal of the European Union L 208/39
ANNEX
BEST AVAILABLE TECHNIQUES (BAT) CONCLUSIONS FOR WASTE
SCOPE
These BAT conclusions concern the following activities specified in Annex I to Directive 2010/75/EU, namely:
— 5.1. Disposal or recovery of hazardous waste with a capacity exceeding 10 tonnes per day involving one or more of the following activities:
(a) biological treatment;
(b) physico-chemical treatment;
(c) blending or mixing prior to submission to any of the other activities listed in points 5.1 and 5.2 of Annex I to Directive 2010/75/EU;
(d) repackaging prior to submission to any of the other activities listed in points 5.1 and 5.2 of Annex I to Directive 2010/75/EU;
(e) solvent reclamation/regeneration;
(f) recycling/reclamation of inorganic materials other than metals or metal compounds; (g) regeneration of acids or bases;
(h) recovery of components used for pollution abatement;
(i) recovery of components from catalysts;
(j) oil re-refining or other reuses of oil;
— 5.3. (a) Disposal of non-hazardous waste with a capacity exceeding 50 tonnes per day involving one or more of the following activities, and excluding activities covered by Council Directive 91/271/EEC (1):
(i) biological treatment;
(ii) physico-chemical treatment;
(iii) pre-treatment of waste for incineration or co-incineration;
(iv) treatment of ashes;
(v) treatment in shredders of metal waste, including waste electrical and electronic equipment and end-of-life vehicles and their components.
(b) Recovery, or a mix of recovery and disposal, of non-hazardous waste with a capacity exceeding 75 tonnes per day involving one or more of the following activities, and excluding activities covered by Directive 91/271/EEC:
(i) biological treatment;
(ii) pre-treatment of waste for incineration or co-incineration;
(iii) treatment of ashes;
(iv) treatment in shredders of metal waste, including waste electrical and electronic equipment and end-of-life vehicles and their components.
When the only waste treatment activity carried out is anaerobic digestion, the capacity threshold for this activity shall be 100 tonnes per day.
— 5.5. Temporary storage of hazardous waste not covered under point 5.4 of Annex I to Directive 2010/75/EU pending any of the activities listed in points 5.1, 5.2, 5.4 and 5.6 of Annex I to Directive 2010/75/EU with a total capacity exceeding 50 tonnes, excluding temporary storage, pending collection, on the site where the waste is generated.
— 6.11. Independently operated treatment of waste water not covered by Directive 91/271/EEC and discharged by an installation undertaking activities covered under points 5.1, 5.3 or 5.5 as listed above.
(1) Council Directive 91/271/EEC of 21 May 1991 concerning urban waste-water treatment (OJ L 135, 30.5.1991, p. 40).
Referring to independently operated treatment of waste water not covered by Directive 91/271/EEC above, these BAT conclusions also cover the combined treatment of waste water from different origins if the main pollutant load originates from the activities covered under points 5.1, 5.3 or 5.5 as listed above.
These BAT conclusions do not address the following:
— Surface impoundment.
— Disposal or recycling of animal carcases or of animal waste covered by the activity description in point 6.5 of Annex I to Directive 2010/75/EU when this is covered by the BAT conclusions on the slaughterhouses and animal by-products industries (SA).
— On-farm processing of manure when this is covered by the BAT conclusions for the intensive rearing of poultry or pigs (IRPP).
— Direct recovery (i.e. without pretreatment) of waste as a substitute for raw materials in installations carrying out activities covered by other BAT conclusions, e.g.:
— Direct recovery of lead (e.g. from batteries), zinc or aluminium salts or recovery of the metals from catalysts. This may be covered by the BAT conclusions for the non-ferrous metals industries (NFM).
— Processing of paper for recycling. This may be covered by the BAT conclusions for the production of pulp, paper and board (PP).
— Use of waste as fuel/raw material in cement kilns. This may be covered by the BAT conclusions for the production of cement, lime and magnesium oxide (CLM).
— Waste (co-)incineration, pyrolysis and gasification. This may be covered by the BAT conclusions for waste incineration (WI) or the BAT conclusions for large combustion plants (LCP).
— Landfill of waste. This is covered by Council Directive 1999/31/EC (1). In particular, underground permanent and long-term storage (≥ 1 year before disposal, ≥ 3 years before recovery) are covered by Directive 1999/31/EC.
— In situ remediation of contaminated soil (i.e. unexcavated soil).
— Treatment of slags and bottom ashes. This may be covered by the BAT conclusions for waste incineration (WI) and/or the BAT conclusions for large combustion plants (LCP).
— Smelting of scrap metals and metal-bearing materials. This may be covered by the BAT conclusions for non-ferrous metals industries (NFM), the BAT conclusions for iron and steel production (IS), and/or the BAT conclusions for the smitheries and foundries industry (SF).
— Regeneration of spent acids and alkalis when this is covered by the BAT conclusions for ferrous metals processing.
— Combustion of fuels when it does not generate hot gases which come into direct contact with the waste. This may be covered by the BAT conclusions for large combustion plants (LCP) or by Directive (EU) 2015/2193 of the European Parliament and of the Council (2).
Other BAT conclusions and reference documents which could be relevant for the activities covered by these BAT conclusions are the following:
— Economics and cross-media effects (ECM);
— Emissions from storage (EFS);
— Energy efficiency (ENE);
— Monitoring of emissions to air and water from IED installations (ROM);
— Production of cement, lime and magnesium oxide (CLM);
— Common waste water and waste gas treatment/management systems in the chemical sector (CWW);
— Intensive rearing of poultry or pigs (IRPP).
These BAT conclusions apply without prejudice to the relevant provisions of EU legislation, e.g. the waste hierarchy.
(1) Council Directive 1999/31/EC of 26 April 1999 on the landfill of waste (OJ L 182, 16.7.1999, p. 1).
(2) Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants (OJ L 313, 28.11.2015, p. 1).

## Definitions
17.8.2018 EN Official Journal of the European Union L 208/41
DEFINITIONS
For the purposes of these BAT conclusions, the following definitions apply:
Term used Definition
General terms
Channelled emissions | Emissions of pollutants into the environment through any kind of duct, pipe, stack, etc. This also includes emissions from open-top biofilters.
Continuous measurement | Measurement using an ‘automated measuring system’ permanently installed on site.
Declaration of cleanliness | Written document provided by the waste producer/holder certifying that the empty waste packaging concerned (e.g. drums, containers) is clean with respect to the acceptance criteria.
Diffuse emissions | Non-channelled emissions (e.g. of dust, organic compounds, odour) which can result from ‘area’ sources (e.g. tanks) or ‘point’ sources (e.g. pipe flanges). This also includes emissions from open-air windrow composting.
Direct discharge | Discharge to a receiving water body without further downstream waste water treatment.
Emissions factors | Numbers that can be multiplied by known data such as plant/process data or throughput data to estimate emissions.
Existing plant | A plant that is not a new plant.
Flaring | High-temperature oxidation to burn combustible compounds of waste gases from industrial operations with an open flame. Flaring is primarily used for burning off flammable gas for safety reasons or during non-routine operating conditions.
Fly ashes | Particles from the combustion chamber or formed within the flue-gas stream, that are transported in the flue-gas.
Fugitive emissions | Diffuse emissions from ‘point’ sources.
Hazardous waste | Hazardous waste as defined in point 2 of Article 3 of Directive 2008/98/EC.
Indirect discharge | Discharge which is not a direct discharge.
Liquid biodegradable waste | Waste of biological origin with a relatively high water content (e.g. fat separator contents, organic sludges, catering waste).
Major plant upgrade | A major change in the design or technology of a plant with major adjustments or replacements of the process and/or abatement technique(s) and associated equipment.
Mechanical biological treatment (MBT) | Treatment of mixed solid waste combining mechanical treatment with biological treatment such as aerobic or anaerobic treatment.
New plant | A plant first permitted at the site of the installation following the publication of these BAT conclusions or a complete replacement of a plant following the publication of these BAT conclusions.
Output | The treated waste exiting the waste treatment plant.
Pasty waste | Sludge which is not free-flowing.
Periodic measurement | Measurement at specified time intervals using manual or automated methods.
Recovery | Recovery as defined in Article 3(15) of Directive 2008/98/EC.
Re-refining | Treatments carried out on waste oil to transform it to base oil.
Regeneration | Treatments and processes mainly designed to make the treated materials (e.g. spent activated carbon or spent solvent) suitable again for a similar use.
Sensitive receptor | Area which needs special protection, such as: — residential areas; — areas where human activities are carried out (e.g. neighbouring workplaces, schools, daycare centres, recreational areas, hospitals or nursing homes).
Surface impoundment | Placement of liquid or sludgy discards into pits, ponds, lagoons, etc.
Treatment of waste with calorific value | Treatment of waste wood, waste oil, waste plastics, waste solvents, etc. To obtain a fuel or to allow a better recovery of its calorific value.
VFCs | Volatile (hydro)fluorocarbons: VOCs consisting of fluorinated (hydro)carbons, in particular chlorofluorocarbons (CFCs), hydrochlorofluorocarbons (HCFCs) and hydrofluorocarbons (HFCs).
VHCs | Volatile hydrocarbons: VOCs consisting entirely of hydrogen and carbon (e.g. ethane, propane, iso-butane, cyclopentane).
VOC | Volatile organic compound as defined in Article 3(45) of Directive 2010/75/EU.
Waste holder | Waste holder as defined in Article 3(6) of Directive 2008/98/EC of the European Parliament and of the Council(1).
Waste input | The incoming waste to be treated in the waste treatment plant.
Water-based liquid waste | Waste consisting of aqueous liquids, acids/alkalis or pumpable sludges (e.g. emulsions, waste acids, aqueous marine waste) which is not liquid biodegradable waste.
Pollutants/parameters
AOX | Adsorbable organically bound halogens, expressed as Cl, include adsorbable organically bound chlorine, bromine and iodine.
Arsenic | Arsenic, expressed as As, includes all inorganic and organic arsenic compounds, dissolved or bound to particles.
BOD | Biochemical oxygen demand. Amount of oxygen needed for the biochemical oxidation of organic and/or inorganic matter in five (BOD5) or in seven (BOD7) days.
Cadmium | Cadmium, expressed as Cd, includes all inorganic and organic cadmium compounds, dissolved or bound to particles.
CFCs | Chlorofluorocarbons: VOCs consisting of carbon, chlorine and fluorine.
Chromium | Chromium, expressed as Cr, includes all inorganic and organic chromium compounds, dissolved or bound to particles.
Hexavalent chromium | Hexavalent chromium, expressed as Cr(VI), includes all chromium compounds where the chromium is in the oxidation state +6.
COD | Chemical oxygen demand. Amount of oxygen needed for the total chemical oxidation of the organic matter to carbon dioxide. COD is an indicator for the mass concentration of organic compounds.
Copper | Copper, expressed as Cu, includes all inorganic and organic copper compounds, dissolved or bound to particles.
Cyanide | Free cyanide, expressed as CN-.
Dust | Total particulate matter (in air).
HOI | Hydrocarbon oil index. The sum of compounds extractable with a hydrocarbon solvent (including long-chain or branched aliphatic, alicyclic, aromatic or alkyl-substituted aromatic hydrocarbons).
HCl | All inorganic gaseous chlorine compounds, expressed as HCl.
HF | All inorganic gaseous fluorine compounds, expressed as HF.
H2S | Hydrogen sulphide. Carbonyl sulphide and mercaptans are not included.
Lead | Lead, expressed as Pb, includes all inorganic and organic lead compounds, dissolved or bound to particles.
Mercury | Mercury, expressed as Hg, includes elementary mercury and all inorganic and organic mercury compounds, gaseous, dissolved or bound to particles.
NH3 | Ammonia.
Nickel | Nickel, expressed as Ni, includes all inorganic and organic nickel compounds, dissolved or bound to particles.
Odour concentration | Number of European Odour Units (ouE) in one cubic metre at standard conditions measured by dynamic olfactometry according to EN 13725.
PCB | Polychlorinated biphenyl.
Dioxin-like PCBs | Polychlorinated biphenyls as listed in Commission Regulation (EC) No 199/2006(2).
PCDD/F | Polychlorinated dibenzo-p-dioxin/furan(s).
PFOA | Perfluorooctanoic acid.
PFOS | Perfluorooctanesulphonic acid.
Phenol index | The sum of phenolic compounds, expressed as phenol concentration and measured according to EN ISO 14402.
TOC | Total organic carbon, expressed as C (in water), includes all organic compounds.
Total N | Total nitrogen, expressed as N, includes free ammonia and ammonium nitrogen (NH4-N), nitrite nitrogen (NO2-N), nitrate nitrogen (NO3-N) and organically bound nitrogen.
Total P | Total phosphorus, expressed as P, includes all inorganic and organic phosphorus compounds, dissolved or bound to particles
TSS | Total suspended solids. Mass concentration of all suspended solids (in water), measured via filtration through glass fibre filters and gravimetry.
TVOC | Total volatile organic carbon, expressed as C (in air).
Zinc | Zinc, expressed as Zn, includes all inorganic and organic zinc compounds, dis­ solved or bound to particles.
(1) Directive 2008/98/EC of the European Parliament and of the Council of 19 November 2008 on waste and repealing certain Directives (OJ L 312, 22.11.2008, p. 3).
(2) Commission Regulation (EC) No 199/2006 of 3 February 2006 amending Regulation (EC) No 466/2001 setting maximum levels for certain contaminants in foodstuffs as regards dioxins and dioxin-like PCBs (OJ L 32, 4.2.2006, p. 34).
For the purposes of these BAT conclusions, the following acronyms apply:
Acronym | Definition
EMS | Environmental management system
EoLVs | End-of-life vehicles (as defined in Article 2(2) of Directive 2000/53/EC of the European Parliament and of the Council(1))
HEPA | High-efficiency particle air (filter)
IBC | Intermediate bulk container
LDAR | Leak detection and repair
LEV | Local exhaust ventilation system
POP | Persistent organic pollutant (as listed in Regulation (EC) No 850/2004 of the European Parliament and of the Council(2))
WEEE | Waste electrical and electronic equipment (as defined in Article 3(1) of Directive 2012/19/EU of the European Parliament and of the Council(3))
(1) Directive 2000/53/EC of the European Parliament and of the Council of 18 September 2000 on end-of life vehicles (OJ L 269, 21.10.2000, p. 34).
(2) Regulation (EC) No 850/2004 of the European Parliament and of the Council of 29 April 2004 on persistent organic pollutants and amending Directive 79/117/EEC (OJ L 158, 30.4.2004, p. 7).
(3) Directive 2012/19/EU of the European Parliament and of the Council of 4 July 2012 on waste electrical and electronic equipment (WEEE) (OJ L 197, 24.7.2012, p. 38).

## General considerations
17.8.2018 EN Official Journal of the European Union L 208/45
GENERAL CONSIDERATIONS Best Available Techniques
The techniques listed and described in these BAT conclusions are neither prescriptive nor exhaustive. Other techniques may be used that ensure at least an equivalent level of environmental protection.
Unless otherwise stated, the BAT conclusions are generally applicable.
Emission levels associated with the best available techniques (BAT-AELs) for emissions to air
Unless stated otherwise, emission levels associated with the best available techniques (BAT-AELs) for emissions to air given in these BAT conclusions refer to concentrations (mass of emitted substances per volume of waste gas) under the following standard conditions: dry gas at a temperature of 273,15 K and a pressure of 101,3 kPa, without correction for oxygen content, and expressed in µg/Nm3 or mg/Nm3.
For averaging periods of BAT-AELs for emissions to air, the following definitions apply.
Type of measurement | Averaging period | Definition
Continuous | Daily average | Average over a period of one day based on valid hourly or half-hourly averages.
Periodic | Average over the sampling period | Average value of three consecutive measurements of at least 30 minutes each(1).
(1) For any parameter where, due to sampling or analytical limitations, a 30-minute measurement is inappropriate, a more suitable measurement period may be employed (e.g. for the odour concentration). For PCDD/F or dioxin-like PCBs, one sampling period of 6 to 8 hours is used.
Where continuous measurement is used, the BAT-AELs may be expressed as daily averages.
Emission levels associated with the best available techniques (BAT-AELs) for emissions to water
Unless stated otherwise, emission levels associated with the best available techniques (BAT-AELs) for emissions to water given in these BAT conclusions refer to concentrations (mass of emitted substances per volume of water), expressed in µg/l or mg/l.
Unless stated otherwise, averaging periods associated with the BAT-AELs refer to either of the following two cases:
— in the case of continuous discharge, daily average values, i.e. 24-hour flow-proportional composite samples;
— in the case of batch discharge, average values over the release duration taken as flow-proportional composite samples, or, provided that the effluent is appropriately mixed and homogeneous, a spot sample taken before discharge.
Time-proportional composite samples can be used provided that sufficient flow stability is demonstrated.
All BAT-AELs for emissions to water apply at the point where the emission leaves the installation.
Abatement efficiency
The calculation of the average abatement efficiency referred to in these BAT conclusions (see Table 6.1) does not include, for COD and TOC, initial treatment steps aiming at separating the bulk organic content from the water-based liquid waste, such as evapo-condensation, emulsion breaking or phase separation.

## BAT 1-5
L 208/46 EN Official Journal of the European Union 17.8.2018 |  |  |  | Southern Water comments and evidence
1. GENERAL BAT CONCLUSIONS
1.1. Overall environmental performance
BAT 1. In order to improve the overall environmental performance, BAT is to implement and adhere to an environmental management system (EMS) that incorporates all of the following features: |  |  |  | Sludge imports | Waste imports
I. commitment of the management, including senior management; |  |  |  | Achieved through the development and implementation of the EMS certified through the ISO 14001: 2015 standard and externally accredited as well as internally audited and reviewed annually to ensure continuing suitability, adequacy, appropriateness and effectiveness. Additional new procedures and updates to relevant existing plans within the system will be undertaken, where necessary, to ensure the requirements and conditions set out the permit are complied with and gaps filled.
II. definition, by the management, of an environmental policy that includes the continuous improvement of the environmental performance of the installation;
III. planning and establishing the necessary procedures, objectives and targets, in conjunction with financial planning and investment;
IV. implementation of procedures paying particular attention to:
(a) structure and responsibility,
(b) recruitment, training, awareness and competence,
(c) communication,
(d) employee involvement,
(e) documentation,
(f) effective process control,
(g) maintenance programmes,
(h) emergency preparedness and response,
(i) safeguarding compliance with environmental legislation;
V. checking performance and taking corrective action, paying particular attention to:
(a) monitoring and measurement (see also the JRC Reference Report on Monitoring of emissions to air and water from IED installations – ROM),
(b) corrective and preventive action,
(c) maintenance of records,
(d) independent (where practicable) internal or external auditing in order to determine whether or not the EMS conforms to planned arrangements and has been properly implemented and maintained;
VI. review, by senior management, of the EMS and its continuing suitability, adequacy and effectiveness;
VII. following the development of cleaner technologies; |  |  |  | Influenced within and outside the business and managed through various teams including wastewater strategy, Bluewave innovation team, energy, procurement, wider commercial roles, process optimisation and Engineering Technical Services (ETS). These teams review and promote the adoption of new technology where potential is identified to improve environmental or commercial performance.
VIII. consideration for the environmental impacts from the eventual decommissioning of the plant at the stage of designing a new plant, and throughout its operating life; |  |  |  | Achieved through the development and implementation of the EMS certified through the ISO 14001: 2015 standard and externally accredited as well as internally audited and reviewed annually to ensure continuing suitability, adequacy, appropriateness and effectiveness. Additional new procedures and updates to relevant existing plans within the system will be undertaken, where necessary, to ensure the requirements and conditions set out the permit are complied with and gaps filled. Whole life considerations are part of design review basis in line with CDM regulations requirements.
IX. application of sectoral benchmarking on a regular basis;
X. waste stream management (see BAT 2);
XI. an inventory of waste water and waste gas streams (see BAT 3);
XII. residues management plan (see description in Section 6.5);
XIII. accident management plan (see description in Section 6.5);
XIV. odour management plan (see BAT 12); |  |  |  | Odour management plans (EMS341 - Air quality/odour management) have been updated and further revisions are to be completed in line with document management requirements (periodic or with cause). This is in line with the requirements within the Technical Guidance Notes (TGNs), and Environment Agency guidance.
XV. noise and vibration management plan (see BAT 17). |  |  |  | No specific noise and vibration management plan has been developed and the requirements for this are covered by other procedures. Most likely cause is a complaint or equipment requiring maintenance. Noise mitigation measures are considered at design stage and look to meet all required legislation. Typical solutions include acoustic enclosures and the utilisation of building are used on some sites, this is reviewed with respect to receptors. During normal operation equipment is routinely check for any increase in noise or vibration, and maintenance jobs raised and carried out where this is the case. Completion of project work is subject to CDM where noise is considered in project execution. Vibration forms a part of equipment testing & maintenance and required to be in line with manufacturers reccomendations.
Applicability
The scope (e.g. level of detail) and nature of the EMS (e.g. standardised or non-standardised) will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed).
BAT 2. In order to improve the overall environmental performance of the plant, BAT is to use all of the techniques given below. |  |  |  | Sludge imports | Waste imports
Technique |  | Description
a. | Set up and implement waste characterisation and pre-acceptance procedures | These procedures aim to ensure the technical (and legal) suitability of waste treatment operations for a particular waste prior to the arrival of the waste at the plant. They include procedures to collect information about the waste input and may include waste sampling and characterisation to achieve sufficient knowledge of the waste composition. Waste pre-acceptance procedures are risk-based considering, for example, the hazardous properties of the waste, the risks posed by the waste in terms of process safety, occupational safety and environmental impact, as well as the information provided by the previous waste holder(s). |  | The Duty of Care procedure is explained 790101_MSD_DutyofCare_FUL February 2024. . All sludges that are processed at the facility are either indigenous primary and secondary sludges from the adjacent WTW, or imported liquid and cake sludge from other WTW's in the region. The volume and dry solids concentration of all sludge imports are recorded via the liquid import logging equipment. We measure flows and dry solids concentrations on the loggers but they are not considered accurate enough to calculate TDS. TDS is calculated at the feed into the digesters where flow and solids concentration is measured (solids being by daily spot samples). Sludges are conventional sludges from the wastewater treatment process and are not routinely tested, other than for those measurements identified above as the composition of domestic sludge is well established. All data is stored on the logger software database. There are no current specific pre-acceptance procedures for sludge imports. A production planning environment has been established with a weekly review of import capacity and CHP availability to optimise sludge operations across the region. This allows redirection of imports to an alternative facility if a given facility has any issue that prevents it from receiving the waste. Each WTW site has an established collection schedule set in agreement with the site manager and process scientist. This ensures sludge is moved at regular intervals dependent on the throughput capacity of the site. Imports to STCs are managed with the site managers agreeing specific import volumes that are not to be exceeded. All waste being treated is non-hazardous sewage sludge. We acknowledge shortcomings in the current arrangements against BAT and are developing a plan to provide to the EA for review within 6 months of permit issue. This will include waste characterisation. The review completed so far has identified a significant impact on the operational arrangements. Significant uncertainty remains regarding some elements of meeting BAT, specifically in relation to: The volume of testing required (install of additional sample points/means of sampling, supply chain capacity and related logistical considerations) The requirement to have results prior to import to STC (re. fleet size, parking capacity, additonal storage capacity required at source, no means to 'stop the flow' at source works) The test requirements (determinands, need for continued tests for a long list and potential rationalisation or amendment once an initial suite of tests is completed) What happens to loads/batches that are outside acceptable testing limits. The plan will include reviewing alternative solutions aligned to the intent of BATs and this will be discussed with the Environment Agency in due course. Due to the overall scale of the operation (~55k sludge traffic movements per year) it is anticipated that a phased approach will be adopted to ensure the measures provide the anticipated The requirements to implement the plan cannot yet be determined, as such we can only commit to implementation by the end of AMP8. Any improvement or update in realtion to this will be provided to the Environment Agency as plans develop. | Pre-acceptance procedure EMS387 - Procedure for the Acceptance of Tankered Waste is used prior to arrival of the waste at the plant to determine the suitability for treatment of new Tankered Waste imports. The pre-acceptance process is completed by a qualified Process Scientist. We acknowledge shortcomings in the current arrangements against BAT and are developing a plan for the revision and implementation of waste pre-acceptance and acceptance. This will be provided for EA review within 6months of permit issue and include waste characterisation. The review completed so far has identified a significant impact on existing operational arrangements. Significant uncertainty remains regarding some elements of meeting BAT, specifically in relation to: The volume of testing required (install of additional sample points/means of sampling, supply chain capacity and related logistical considerations) The requirement to have results prior to import to STC (re. fleet size, parking capacity, additonal storage capacity required at source, no means to 'stop the flow' at source works) The test requirements (determinands, need for continued tests for a long list and potential rationalisation or amendment once an initial suite of tests are completed) What happens to loads/batches that are outside acceptable testing limits. Existing commercial arrangements and timescales for implementation of change. The plan will include reviewing alternative solutions aligned to the intent of BATs and this will be discussed with the EA in due course. The requirements to implement the plan cannot yet be determined, as such we can only commit to implementation by the end of AMP8. Any improvement or update in realtion to this will be provided to the EA as plans develop.
b. | Set up and implement waste acceptance procedures | Acceptance procedures aim to confirm the characteristics of the waste, as identified in the pre-acceptance stage. These procedures define the elements to be verified upon the arrival of the waste at the plant as well as the waste acceptance and rejection criteria. They may include waste sampling, inspection and analysis. Waste acceptance procedures are risk-based considering, for example, the hazardous properties of the waste, the risks posed by the waste in terms of process safety, occupational safety and environmental impact, as well as the information provided by the previous waste holder(s).
c. | Set up and implement a waste tracking system and inventory | A waste tracking system and inventory aim to track the location and quantity of waste in the plant. It holds all the information generated during waste pre-acceptance procedures (e.g. date of arrival at the plant and unique reference number of the waste, information on the previous waste holder(s), pre-acceptance and acceptance analysis results, intended treatment route, nature and quantity of the waste held on site including all identified hazards), acceptance, storage, treatment and/or transfer off site. The waste tracking system is risk-based considering, for example, the hazardous properties of the waste, the risks posed by the waste in terms of process safety, occupational safety and environmental impact, as well as the information provided by the previous waste holder(s). |  | Imports of liquid sludge are tracked by a logging system which records the location of origin, volume, date, time and dry solids (%). The record of each imported consignment is linked to the tanker. Cake imports are similarly received with roll-on-roll off loads. The intended treatment route is known on receipt. Once the waste is received at the facility it becomes part of the overall inventory for the site and, due to mixing, it is not possible to track a specific load. Digested sludge is dewatered and either stored in cake bays or where lime treated, removed immediately off site and taken to a farm. The sludge treatment, dewatering and storage procedure are set out in the Hazard Analysis and Critical Control Point (HACCP) Plan, a copy of which is kept on the site. The treated sludge exported for agricultural use is recorded in BioSolids Integrated Operations (BIO), in line with the record keeping requirements set out in the Sludge (Use in Agriculture) Regs, including: • quantity of sludge produced • quantity of sludge supplied • sludge test results (batch sample/ test to SUIA requirements) • type of sludge treatment use • final location of sludge use Whilst the waste is considered to be tracked and most other information variously recorded it is recognised that the systems used are not able to provide the reporting required. At this stage this is thought to be largely a collation of data and reporting issue to which we are looking to apply a technology solution. The development of the plan will help identify any specific shortcomings and implementation of the measures required is likely to involve project delivery. This is linked to the waste charaterisation requirements and the solutions adopted will be suitable for both needs. A Waste Reporting & Tracking plan will be provided within 6 months of permit issue and we will look to implement the requirements therein within 12 months of the agreed plan and no later than the end of AMP8. | Tankered waste is not physically tracked through the plant once the disposal transaction is completed at the dedicated Tankered waste reception facility. Transaction data including date of arrival and unique reference number of the waste is recorded during this process. This import then forms part of the STC inventory and measures will be taken taken in line with comments provided to the left.
d. | Set up and implement an out­ put quality management sys­ tem | This technique involves setting up and implementing an output quality management system, so as to ensure that the output of the waste treat­ ment is in line with the expectations, using for example existing EN standards. This management system also allows the performance of the waste treatment to be monitored and optimised, and for this purpose may include a material flow analysis of relevant components through­ out the waste treatment. The use of a material flow analysis is risk-based considering, for example, the azardous properties of the waste, the risks posed by the waste in terms of process safety, occupational safety and environmental impact, as well as the information provided by the previous waste holder(s). |  | Biosolids is the main output from the STCs and this is treated to meet the requirements of the various regulations, codes of practice surrounding sludge recycling, including Sludge (Use in Agriculture) Regulations 1989 (SUIA). One of the key requirements is to meet the HACCP requirements as part of the Safe Sludge Matrix. The quality of the treated sludge is controlled prior to being exported for use in agriculture through the procedure set out in the HACCP and is used to reduce the risk of safety hazards in the food crops produced. This ensures bacti compliance of the final material. Each site has its own HACCP plan detailing the critical control points to be achieved. Adherence to the CCPs is managed via the Sludge Management System where retention times, digester temperatures and also pH are recorded. After a period of time stored in the cake bays, the material is sampled to ensure its suitability for application to land under SUIA Internal quality requirements not formally documented but seek to ensure a dry solids of the final material of approx 25% DS. Other waste streams, eg. grit are subject to further requirements for exporting. Whilst SUIA etc is followed and some parameters are measured to ensure digestion optimisation, it is acknowledged that it does not meet BAT. No specific plan will be drafted for this for submission to the Environment Agency as it is considered to be more appropriate to include in other plans (eg. monitoring). The findings from detailed evaluation will be included in other plans to ensure the route to compliance for this requirement is appropriately documented, this includes additional digestion monitoring and sampling & testing.
e. | Ensure waste segregation | Waste is kept separated depending on its properties in order to enable easier and environmentally safer storage and treatment. Waste segregation relies on the physical separation of waste and on procedures that identify when and where wastes are stored. |  | Final biosolids where stored on site are kept in maturation bays. Close control is maintained of these bays as for these sites the maturation times are part of the HACCP plans. Material is only released for recycling to agriculture at the end of the maturation period and when the biosolids has been tested to ensure it meets the bacti standards. Other waste (plastics, metals, WEEE etc) is physically segregated in line with disposal requirements. Site management is responsible for ensuring the demand for waste storage is appropriate for the facility capacity and collection and disposal is completed on a regular basis with the facility to request additonal collection(s) if/as required. Improvements to meet tracking and reporting requirements will be undertaken in line with the inventory BAT. | Tankered waste imports utilise vehicles and therefore are segregated prior to import. Once discharged to the facility they are considerd to form part of the facility inventory and are managed in line with comments on the left.
f. | Ensure waste compatibility prior to mixing or blending of waste | Compatibility is ensured by a set of verification measures and tests in order to detect any unwanted and/or potentially dangerous chemical reactions between wastes (e.g. polymerisation, gas evolution, exothermal reaction, decomposition, crystallisation, recipitation) when mixing, blending or carrying out other treatment operations. The compatibility tests are risk-based considering, for example, the hazardous properties of the waste, the risks posed by the waste in terms of process safety, occupational safety and environmental impact, as well as the information provided by the previous waste holder(s). |  | There are no specific blending / compatibility measures established for the majority of the waste imported. When considering a 'septic' sludge import there are specific considerations regarding the composition and the potential for adverse impact to the sludge treatment process. Where chemicals are utilised it it in line with accepted practice and process scientist review. We are not in a position to demonstrate BAT compliance, this BAT will be covered in the waste characterisation plan and will include ensuring appropriate process documentation. The outcomes of the waste characterisation are required to determine the route to compliance, as such the implemntation of measures will follow the same timescales. The data collated through characterisation will inform the risk assessment basis for future receipts. | Hazardous waste assessments are undertaken as part of the tankered waste pre-acceptance process which uses the Environment Agency WM3 Guidance to confirm weather the waste code is hazardous or non-hazardous. Hazardous wastes are subject to specific controls. Further work is required to domonstrate compliance and this will be covered in the waste characterisation plan and will include ensuring appropriate documentation. The data collated through characterisation will inform modifications to the risk assessment basis used for future receipts.
g. | Sort incoming solid waste | Sorting of incoming solid waste(1) aims to prevent unwanted material from entering subsequent waste treatment process(es). It may include: — manual separation by means of visual examinations; — ferrous metals, non-ferrous metals or all-metals separation; — optical separation, e.g. by near-infrared spectroscopy or X-ray systems; — density separation, e.g. by air classification, sink-float tanks, vibra­ tion tables; — size separation by screening/sieving. |  | All sludge is screened after import to recognised standards, this removes unwanted material from the process. Screenings are contained in suitable containers and removed from site. | All waste imports are screened after being received so if there are any solid material in the imports then this will be removed through this process.
(1) Sorting techniques are described in Section 6.4
BAT 3. In order to facilitate the reduction of emissions to water and air, BAT is to establish and to maintain an inventory of waste water and waste gas streams, as part of the environmental management system (see BAT 1), that incorporates all of the following features: |  |  |  | Sludge imports | Waste imports
(i) information about the characteristics of the waste to be treated and the waste treatment processes, including: |  |  |  | The main emissions referred to here are the wastewater and gas emissions form the STC. For the wastewater there are a number of sources - * centrate from the thickening process where liquid sludge is thickened to a target dry solids of 7% before being fed into the anaerobic digestion plant * centrate from the dewatering process where digested liquid sludge is turned into biosolids at approx 25% dry solids * wastewater is also generated from washing down of screens and also surface water All wastewater generated by the STC process is passed to the WTW for full treatment before being discharged to the environment, the discharge being controlled by the UWWTD. A number of emissions to air have been identified and are included in out development of plans. Refer to EMS 480 for all waste streams generated by SWS, as well as the information in the main supporting document
(a) simplified process flow sheets that show the origin of the emissions; |  |  |  | Process Flow diagrams have been provided as part of the permit application
(b) descriptions of process-integrated techniques and waste water/waste gas treatment at source including their performances; |  |  |  | All wastewater produced from the STC process is returned to the WWTW for full treatment. All relevant wastes (liquor returns and biogas) are well known and understood as waste streams by SWS as they are produced, handled and treated on all of its STCs. Note we only produce biogas on our 16 STCs
(ii) information about the characteristics of the waste water streams, such as: |  |  |  | As an interim measure we have established a sampling programme based on existing sampling points and substance test list based on our initial understanding. We accept this does not currently meet BAT but anticipate it may provide additional useful data to inform future plans. Development of a waste characterisation and monitoring plans has commenced and we will provide this within 6 months of permit issue for Environment Agency review. Our considerations include the requirements listed and the following broader requirements to meet BAT: provision of appropriate new sample points a sampling and testing programme to provide the required data to complete a review of the results Procedure for samples found to be out of limits Flow measurement requirements Fate of streams The plan will include outline solutions regarding how BAT can be met. The specific measures required to meet BAT remain subject to the agreed plan and appropriate design, install is thought to be achievable before the end of 2027 but no later than the end of AMP8.
(a) average values and variability of flow, pH, temperature, and conductivity;
(b) average concentration and load values of relevant substances and their variability (e.g. COD/TOC, nitrogen species, phosphorus, metals, priority substances/micropollutants);
(c) data on bioeliminability (e.g. BOD, BOD to COD ratio, Zahn-Wellens test, biological inhibition potential (e.g. inhibition of activated sludge)) (see BAT 52);
(iii) information about the characteristics of the waste gas streams, such as:
(a) average values and variability of flow and temperature;
(b) average concentration and load values of relevant substances and their variability (e.g. organic compounds, POPs such as PCBs);
(c) flammability, lower and higher explosive limits, reactivity;
(d) presence of other substances that may affect the waste gas treatment system or plant safety (e.g. oxygen, nitrogen, water vapour, dust).
Applicability
The scope (e.g. level of detail) and nature of the inventory will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed).
BAT 4. In order to reduce the environmental risk associated with the storage of waste, BAT is to use all of the techniques given below. |  |  |  | Sludge imports | Waste imports
Technique |  | Description | Applicability
a. | Optimised storage location | This includes techniques such as: — the storage is located as far as technically and economically possible from sensitive receptors, watercourses, etc.; — the storage is located in such a way so as to eliminate or minimise the unnecessary handling of wastes within the plant (e.g. the same wastes are handled twice or more or the transport distances on site are unnecessarily long). | Generally applicable to new plants. | The site was constructed prior to the introduction of IED/BAT and therefore these issues were not formally considered as part of the design process. Unfortunately the site location and design is not ideal to meet BAT but the cost to rebuild the facility is considered prohibitively expensive and targeted retrospective works are more cost effective. The site reduces the unccessary handling of non-liquid wastes by collating it in appropriate storage areas prior to use, during and and when ready for disposal.
b. | Adequate storage capacity | Measures are taken to avoid accumulation of waste, such as: — the maximum waste storage capacity is clearly established and not exceeded taking into account the characteristics of the wastes (e.g. regarding the risk of fire) and the treatment capacity; — the quantity of waste stored is regularly monitored against the maximum allowed storage capacity; — the maximum residence time of waste is clearly established. | Generally applicable. | Tank level monitors and tracking of transfers allows us to manage the quantity of waste stored. Digestor monitoring includes residence time. The STC receives indiginous sludge flows from the WtW which is operated by the same company, as such the sites are able to manage flows and capacity on a common basis. Storage capacity is provided for the anticipated flows. Cake bay areas are sized for the throughput of the site and utilised in a sequence, upon reaching the required quality the cake is removed from site. Storage within the bays is controlled and when capacity is at risk of being exceeded waste will be moved off site to other sites for storage, if necessary, to avoid exceeding site storage capacities or where safe to do so spread to land. Should a facility experience an issue that restricts storage capacity operational trigger levels help us control the flow of wastes and manage the overall operation between sites. Other waste incidental to the processes are kept on-site and regularly removed by a waste contractor either periodically or at request as needs determine. Based on feedback to other permits it is anticiapted that this needs to be summarised in a report/plan. We will complete a Wastewater & Digestate buffer storage plan within 6 months of permit issue and provide it to the Environment Agency for review. The content will reflect the topics outlined in this BAT. The arrangements for condensate are not currently BAT compliant. A waste sampling plan outlining measures to meet BAT will be provided within 6 months of permit issue.
c. | Safe storage operation | This includes measures such as: — equipment used for loading, unloading and storing waste is clearly documented and labelled; — wastes known to be sensitive to heat, light, air, water, etc. are protected from such ambient conditions; — containers and drums are fit for purpose and stored securely. |  | Site operational personnel and visitors follow a number of operating procedures that provide the basis for a safe operation. This is proportional to the nature of the work to be completed and includes site familiarisation, permit to work and PPE. Site equipment is subject to a number of maintenance activities, inspections and tests depending on its type. This includes (but is not limited to!) statutory testing and certification like lifting equipment (LOLER), hazardous areas (DSEAR), gas safety and electrical safety. Operatives are trained for activities they are required to undertake. Additionally Southern Water undertakes a planned preventative maintenance programme based on equipment type. This looks to ensure the equipment provided is suitable for use and the remaining asset life is understood. A broad suite of company systems and documentation provides the detail of all measures in relation to this. These are reviewed and audited in line with the relevant certification requirements. Signage is used extensively on site to warn of specific area hazards and, where appropriate for the hazard, means of prevention of entry (eg. hazardous areas. Chemicals and oils are stored in bunded areas, on portable bunds or within enclosed areas to ensure the appropriate containment and avoid the risk of spillages. Chemical handling is subject to COSHH assesment and related safe use procedures including PPE requirements.
d. | Separate area for storage and handling of packaged hazardous waste | When relevant, a dedicated area is used for storage and handling of packaged hazardous waste. |  | Waste is handled in line with documented COSHH requirements. Wastes are segregated for storage.
BAT 5. In order to reduce the environmental risk associated with the handling and transfer of waste, BAT is to set up and implement handling and transfer procedures. |  |  |  | Sludge imports | Waste imports
Description
Handling and transfer procedures aim to ensure that wastes are safely handled and transferred to the respective storage or treatment. They include the following elements: |  |  |  | It is accepted that further development of the existing handling and transfer procedures are required to meet BAT, particularly in relation to sludge imports and on-site operations. This will interface with other elements of scope, as such the updates required remain subject to timescales for other plans, eg. Digestate Storage & Buffer, Reporting, Monitoring and Sampling. The required procedures will be developed and implemented within 12 months of agreement of the above plans. This will be supported by/relate to: The development and implementation of the EMS and certification thereof to ISO 14001:2015 external accreditation and internal audit. This will be reviewed annually to ensure continuing suitability, adequacy, appropriateness and effectiveness. Relevant employees will receive training to either WAMITAB or a new Competency Management System which covers all these elements. Reporting This will include a review and likely update of the existing company procedures to reflect BAT: EMS363 - Procedure for Managing Oil Spills on Sites, EMS364 - Lime Spill Management Procedure, EMS360 - Pollution Prevention Procedure. | Employees accepting tankered waste imports are trained in waste acceptance procedures.
— handling and transfer of waste are carried out by competent staff;
— handling and transfer of waste are duly documented, validated prior to execution and verified after execution; |  |  |  |  | Tankered waste handling and transfer is documented, validated as part of the waste acceptance procedure. If it does not conform to the acceptance procedure it is rejected from site following EMS488 - Waste Rejection and Incident Note
— measures are taken to prevent, detect and mitigate spills; |  |  |  |  | Measures are in place to prevent, detect and mitigate spills as part of the waste acceptance procedure.
— operation and design precautions are taken when mixing or blending wastes (e.g. vacuuming dusty/powdery wastes). |  |  |  |  | N/A
Handling and transfer procedures are risk-based considering the likelihood of accidents and incidents and their environmental impact. |  |  |  |  | Tankered waste imports are risk assessed to reduce the likelihood of accidents, incidents and their environmental impact.

## BAT 6-11
L 208/52 EN Official Journal of the European Union 17.8.2018
1.2. Monitoring
BAT 6. For relevant emissions to water as identified by the inventory of waste water streams (see BAT 3), BAT is to monitor key process parameters (e.g. waste water flow, pH, temperature, conductivity, BOD) at key locations (e.g. at the inlet and/or outlet of the pretreatment, at the inlet to the final treatment, at the point where the emission leaves the installation).
This site does not currently meet this BAT requirement As an interim measure we have established a sampling programme based on existing sampling points and substance test list based on our initial understanding. This is currently under review regarding the latest guidance on determinands. We accept this does not currently meet BAT but anticipate it may provide additional useful data to inform future plans. We are developing a wastewater sampling plan and this will be available within 6 months of permit issue. The plan will be implemented within 12 months of permit issue. We plan to meet BAT through implementing the required sampling and testing at appropriate locations on site. Our plans are being developed based on a phased approach to provide data as soon as available. We are revising the substance list to the guidance provided and looking to implement the revised list as soon as possible. At this stage we are not able to understand the full scope required regarding lab facilities to provide BAT compliant testing but plan to test what we can and investigate options for any other requirements. We are limited by the number of existing sampling points and our plans include scopes of work to physically provide the required equipment to complete all required samples and flow measurements. We will undertake further survey and design to determine the technical requirements for a given site and identify a detailed scope of requirements to meet the specifications required. Our initial review has identified some challenges that we are working to resolve, specifically in relation to MCerts, composite sampling, batched flows and existing pipework geometry. Monitoring locations for each sampling point have been added to the site layout plan. The exact locations remain subject to design development and appropriate documentation will be provided in due course. Development of a sampling plan has commenced and we will be in a position to provide this within 6 months of permit issue.
BAT 7. BAT is to monitor emissions to water with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality.
Substance/parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency(1)(2) | Monitoring associated with | Daily spot samples are taken from centrate lines for solids (TSS). This site does not currently meet this BAT requirement. As an interim measure we have established a sampling programme based on existing sampling points and substance test list based on our initial understanding. We accept this does not currently meet BAT but anticipate it may provide additional useful data to inform future plans. We are developing a wastewater sampling plan and this will be available within 6 months of permit issue. The plan will be implemented within 12 months of permit issue but caution that some more complex elements may take longer, but are to be completed before the end of 2027. The plan will look to characterise the waste and establish a longer term routine operational testing basis. This may include consideration of scenarios where if a substance is identified as not present in the sludge liquors ongoing monitoring is proposed to omit this parameter, as it would be deemed not applicable to the site. Confirmation on omitted parameters to be agreed with the Environment Agency through the sampling plan. We plan to meet BAT through implementing the required sampling and testing at appropriate locations on site. Our plans are being developed based on a phased approach to provide data as soon as available. We are revising the substance list to the guidance provided and looking to implement the revised list as soon as possible. At this stage we are not able to understand the full scope required regarding lab facilities to provide BAT compliant testing but plan to test what we can and investigate options for any other requirements. We are limited by the number of existing sampling points and our plans include scopes of work to physically provide the required equipment to complete all required samples and flow measurements. We will undertake further survey and design to determine the technical requirements for a given site and identify a detailed scope of requirements to meet the specifications required. Our initial review has identified some challenges that we are working to resolve, specifically in relation to MCerts, composite sampling, batched flows and existing pipework geometry. Monitoring locations for each sampling point have been added to the site layout plan. The exact locations remain subject to design development and appropriate documentation will be provided in due course.
Adsorbable organically bound halogens (AOX)(3)(4) | EN ISO 9562 | Treatment of water-based liquid waste | Once every day | BAT 20 | Not presently undertaken but will be included in testing plan
Benzene, toluene, ethylbenzene, xylene (BTEX)(3)(4) | EN ISO 15680 | Treatment of water-based liquid waste | Once every month |  | Not presently undertaken but will be included in testing plan
Chemical oxygen demand (COD)(5)(6) | No EN standard available | All waste treatments except treatment of water-based liquid waste | Once every month |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Free cyanide (CN-)(3)(4) | Various EN standards available (i.e. EN ISO 14403-1 and -2) | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Hydrocarbon oil index (HOI)(4) | EN ISO 9377-2 | Mechanical treatment in shredders of metal waste | Once every month |  | N/A
|  | Treatment of WEEE containing VFCs and/or VHCs |  |  | N/A
|  | Re-refining of waste oil |  |  | N/A
|  | Physico-chemical treatment of waste with calorific value |  |  | N/A
|  | Water washing of excavated contaminated soil |  |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Arsenic (As), Cadmium (Cd), Chromium (Cr), Copper (Cu), Nickel (Ni), Lead (Pb), Zinc (Zn)(3)(4) | Various EN standards available (e.g. EN ISO 11885, EN ISO 17294-2, EN ISO 15586) | Mechanical treatment in shredders of metal waste | Once every month |  | N/A
|  | Treatment of WEEE containing VFCs and/or VHCs |  |  | N/A
|  | Mechanical biological treatment of waste |  |  | N/A
|  | Re-refining of waste oil |  |  | N/A
|  | Physico-chemical treatment of waste with calorific value |  |  | N/A
|  | Physico-chemical treatment of solid and/or pasty waste |  |  | N/A
|  | Regeneration of spent solvents |  |  | N/A
|  | Water washing of excavated con­ taminated soil |  |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Manganese (Mn)(3)(4) |  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Hexavalent chromium (Cr(VI))(3)(4) | Various EN standards available (i.e. EN ISO 10304-3, EN ISO 23913) | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Mercury (Hg)(3)(4) | Various EN standards available (i.e. EN ISO 17852, EN ISO 12846) | Mechanical treatment in shredders of metal waste | Once every month |  | N/A
|  | Treatment of WEEE containing VFCs and/or VHCs |  |  | N/A
|  | Mechanical biological treatment of waste |  |  | N/A
|  | Re-refining of waste oil |  |  | N/A
|  | Physico-chemical treatment of waste with calorific value |  |  | N/A
|  | Physico-chemical treatment of solid and/or pasty waste |  |  | N/A
|  | Regeneration of spent solvents |  |  | N/A
|  | Water washing of excavated con­ taminated soil |  |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
PFOA(3) | No EN standard available | All waste treatments | Once every six months |  | Not presently undertaken but will be included in testing plan
PFOS(3) |  |  |  |  | Not presently undertaken but will be included in testing plan
Phenol index(6) | EN ISO 14402 | Re-refining of waste oil | Once every month |  | N/A
|  | Physico-chemical treatment of waste with calorific value |  |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Total nitrogen (Total N)(6) | EN 12260, EN ISO 11905-1 | Biological treatment of waste | Once every month |  | N/A
|  | Re-refining of waste oil |  |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | None
Total organic carbon (TOC)(5)(6) | EN 1484 | All waste treatments except treatment of water-based liquid waste | Once every month |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Total phosphorus (Total P)(6) | Various EN standards available (i.e. EN ISO 15681-1 and -2, EN ISO 6878, EN ISO 11885) | Biological treatment of waste | Once every month |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Not presently undertaken but will be included in testing plan
Total suspended solids (TSS)(6) | EN 872 | All waste treatments except treatment of water-based liquid waste | Once every month |  | N/A
|  | Treatment of water-based liquid waste | Once every day |  | Daily spot samples from centrate lines.
(1) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(2) In the case of batch discharge less frequent than the minimum monitoring frequency, monitoring is carried out once per batch.
(3) The monitoring only applies when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(4) In the case of an indirect discharge to a receiving water body, the monitoring frequency may be reduced if the downstream waste water treatment plant abates the pollutants concerned.
(5) Either TOC or COD is monitored. TOC is the preferred option, because its monitoring does not rely on the use of very toxic compounds.
(6) The monitoring applies only in the case of a direct discharge to a receiving water body.
BAT 8. BAT is to monitor channelled emissions to air with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality.
Substance/Parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency(1) | Monitoring associated with | We acknowledge our current testing regime does not meet BAT and are developing a monitoring plan to provide to the Environment Agency for review within 6 months of permit issue. The measures outlined in the plan will commence within 12 months of plan agreement. We have undertaken additonal exhaust testing to inform the permit application air quality risk assessement (AQRA). The following is tested for CHP exhausts: NOX, CO, SO2, VOC and non methane VOC. Additionally we plan to complete optical gas imaging to evaluate fugitive emissions and undertake remedial work where required.
| No EN standard available | Mechanical treatment in shredders of metal waste | Once every year | BAT 25 | N/A
CFCs | No EN standard available | Treatment of WEEE containing VFCs and/or VHCs | Once every six months | BAT 29 | N/A
Dioxin-like PCBs | EN 1948-1, -2, and -4(3) | Mechanical treatment in shredders of metal waste(2) | Once every year | BAT 25 | N/A
|  | Decontamination of equipment con­ taining PCBs | Once every three months | BAT 51 | N/A
Dust | EN 13284-1 | Mechanical treatment of waste | Once every six months | BAT 25 | Not presently undertaken but will be included in testing plan
|  | Mechanical biological treatment of waste |  | BAT 34 | Not presently undertaken but will be included in testing plan
|  | Physico-chemical treatment of solid and/or pasty waste |  | BAT 41 | N/A
|  | Thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil |  | BAT 49 | N/A
|  | Water washing of excavated con­ taminated soil |  | BAT 50 | N/A
HCl | EN 1911 | Thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil(2) | Once every six months | BAT 49 | N/A
|  | Treatment of water-based liquid waste(2) |  | BAT 53 | Not presently undertaken but will be included in testing plan
HF | No EN standard available | Thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil(2) | Once every six months | BAT 49 | N/A
Hg | EN 13211 | Treatment of WEEE containing mer­ cury | Once every three months | BAT 32 | N/A
H2S | No EN standard available | Biological treatment of waste(4) | Once every six months | BAT 34 | Not presently undertaken but will be included in testing plan
Metals and metalloids except mercury (e.g. As, Cd, Co, Cr, Cu, Mn, Ni, Pb, Sb, Se, Tl, V)(2) | EN 14385 | Mechanical treatment in shredders of metal waste | Once every year | BAT 25 | N/A
NH3 | No EN standard available | Biological treatment of waste(4) | Once every six months | BAT 34 | Not presently undertaken but will be included in testing plan
|  | Physico-chemical treatment of solid and/or pasty waste(2) | Once every six months | BAT 41 | N/A
|  | Treatment of water-based liquid waste(2) |  | BAT 53 | Not presently undertaken but will be included in testing plan
Odour concentration | EN 13725 | Biological treatment of waste(5) | Once every six months | BAT 34 | Not presently undertaken, SW is likely to monitor H2S and NH3 as alternative acceptable monitoring.
PCDD/F(2) | EN 1948-1, -2 and -3(3) | Mechanical treatment in shredders of metal waste | Once every year | BAT 25 | N/A
TVOC | EN 12619 | Mechanical treatment in shredders of metal waste | Once every six months | BAT 25 | N/A
|  | Treatment of WEEE containing VFCs and/or VHCs | Once every six months | BAT 29 | N/A
|  | Mechanical treatment of waste with calorific value(2) | Once every six months | BAT 31 | Requires expansion to be completed at all sites
|  | Mechanical biological treatment of waste | Once every six months | BAT 34 | Requires expansion to be completed at all sites
|  | Physico-chemical treatment of solid and/or pasty waste(2) | Once every six months | BAT 41 | N/A
|  | Re-refining of waste oil |  | BAT 44 | N/A
|  | Physico-chemical treatment of waste with calorific value |  | BAT 45 | N/A
|  | Regeneration of spent solvents |  | BAT 47 | N/A
|  | Thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil |  | BAT 49 | N/A
|  | Water washing of excavated con­ taminated soil |  | BAT 50 | N/A
|  | Treatment of water-based liquid waste(2) |  | BAT 53 | N/A
|  | Decontamination of equipment con­ taining PCBs(6) | Once every three months | BAT 51 | N/A
(1) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(2) The monitoring only applies when the substance concerned is identified as relevant in the waste gas stream based on the inventory mentioned in BAT 3.
(3) Instead of EN 1948-1, sampling may also be carried out according to CEN/TS 1948-5.
(4) The odour concentration may be monitored instead.
(5) The monitoring of NH3 and H2S can be used as an alternative to the monitoring of the odour concentration. (6) The monitoring only applies when solvent is used for cleaning the contaminated equipment.
BAT 9. BAT is to monitor diffuse emissions of organic compounds to air from the regeneration of spent solvents, the decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery of their calorific value, at least once per year using one or a combination of the techniques given below. |  |  |  |  | N/A
Technique |  | Description
a | Measurement | Sniffing methods, optical gas imaging, solar occultation flux or differential absorption. See descriptions in Section 6.2. |  |  | N/A
b | Emissions factors | Calculation of emissions based on emissions factors, periodically validated (e.g. once every two years) by measurements. |  |  | N/A
c | Mass balance | Calculation of diffuse emissions using a mass balance considering the solvent input, channelled emissions to air, emissions to water, the solvent in the process output, and process (e.g. distillation) residues. |  |  | N/A
BAT 10. BAT is to periodically monitor odour emissions.
Description
Odour emissions can be monitored using: |  |  |  |  | Monitoring of odour emissions will be in line with specific requirements contained in the relevant odour management plans and where odour is considered an issue in the Environmental Risk Assessments.
— EN standards (e.g. dynamic olfactometry according to EN 13725 in order to determine the odour concen­ tration or EN 16841-1 or -2 in order to determine the odour exposure);
— when applying alternative methods for which no EN standards are available (e.g. estimation of odour impact), ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality.
The monitoring frequency is determined in the odour management plan (see BAT 12).
Applicability
The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated.
BAT 11. BAT is to monitor the annual consumption of water, energy and raw materials as well as the annual generation of residues and waste water, with a frequency of at least once per year.
Description
Monitoring includes direct measurements, calculation or recording, e.g. using suitable meters or invoices. The monitoring is broken down at the most appropriate level (e.g. at process or plant/installation level) and considers any significant changes in the plant/installation. |  |  |  |  | Consumption is monitored through various systems, it is accepted that current arrangements do not meet BAT. A plan to meet BAT will be developed and provided to the Environment Agency within 6 months of permit issue. The requirements therein will be implemented within 18 months of the agreed plan. Additional meters are required to be able to report the required information and the data needs to be collated to provide the reporting required.
Water |  |  |  |  | Site overall Consumption regularly monitored against budget but there are no formal procedures in place. Currently consumption is measured on a site basis as no 'sub metering' on site.
Energy |  |  |  |  | Site overall Consumption regularly monitored against budget. Due to lack of sub metering process unit consumption can not be easily identified.
Raw materials (Chemicals) |  |  |  |  | Consumption of the various chemicals used through the STC process are regularly monitored against budget. The SCADA system also includes the ability to monitor raw material usage such as chemicals on some sites.

## BAT 12-16
L 208/56 EN Official Journal of the European Union 17.8.2018
1.3. Emissions to air
BAT 12. In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to set up, implement and regularly review an odour management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements:
— a protocol containing actions and timelines; |  |  |  | EMS 275, 341 air quality and odour management. Odour management plans and reviews are external to the SWS EMS. Odour is reviewed as part of the second line of assurance within the EMS audit programme. Air quality meetings were held within Southern Water involving different stakeholders within the business. Actions and timescales are set.
— a protocol for conducting odour monitoring as set out in BAT 10; |  |  |  | There is a detailed master odour management plan and bespoke odour management plans for some permitted sites where odour is an issue. The protocol for conducting odour monitoring is set out in these plans.
— a protocol for response to identified odour incidents, e.g. complaints; |  |  |  | EMS 341 air quality and odour management sets out the process for responding to odour complaints arising from customer contact (e.g. CSMS).
— an odour prevention and reduction programme designed to identify the source(s); to characterise the contributions of the sources; and to implement prevention and/or reduction measures. |  |  |  | Additional monitoring wil be undertaken in line with the monitoring plan we will provide as outlined elsewhere herein. The results from monitoring will help understand risks and odour sources and allow us to determine the required prevention/reduction measures.
Applicability
The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated.
BAT 13. In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to use one or a combination of the techniques given below.
Technique |  | Description | Applicability
a. | Minimising residence times | Minimising the residence time of (potentially) odorous waste in storage or in handling systems (e.g. pipes, tanks, containers), in particular under anaerobic conditions. When relevant, adequate provisions are made for the acceptance of seasonal peak volumes of waste. | Only applicable to open systems. | We look to move waste off site as soon as practically possible whilst considering prevailing weather and safe access to farm storage (for cake). All digestors are covered and connected to gas systems. As part of wider requirements to meet BAT open processes will be enclosed and appropriate abatement provided where testing and monitoring determines it is required.
b. | Using chemical treatment | Using chemicals to destroy or to reduce the formation of odorous compounds (e.g. To oxidise or to precipitate hydrogen sulphide). | Not applicable if it may hamper the desired output quality. | Chemicals are typically used within odour control units (OCU) The OCU used at this site can be found in the Odour Management PLan Section 4.1 Some sites use ferric dosing to improve settlement characteristics within the treatment process although this does impact on odour potential. A review of OCU performance will be completed as part of the monitoring plan referenced elsewhere herein.
c. | Optimising aerobic treat­ meant | In the case of aerobic treatment of water- based liquid waste, it may include: — use of pure oxygen; — removal of scum in tanks; — frequent maintenance of the aeration system. In the case of aerobic treatment of waste other than water-based liquid waste, see BAT 36. | Generally applicable. | The aerobic (biological ) treatment stage of the main wastewater treatment process is not part of the STC site.
BAT 14. In order to prevent or, where that is not practicable, to reduce diffuse emissions to air, in particular of dust, organic compounds and odour, BAT is to use an appropriate combination of the techniques given below.
Depending on the risk posed by the waste in terms of diffuse emissions to air, BAT 14d is especially relevant.
Technique |  | Description | Applicability
a. | Minimising the number of potential diffuse emission sources | This includes techniques such as: — appropriate design of piping layout (e.g. minimising pipe run length, reducing the number of flanges and valves, using welded fittings and pipes); — favouring the use of gravity transfer rather than using pumps; — limiting the drop height of material; — limiting traffic speed; — using wind barriers. | Generally applicable. | The site was constructed prior to IED, as such we are not able to demonstrate such design considerations were formally considered. Diffuse emissions from open storage areas are discussed in Section 4.2.1 of the Odour Management Plan. Pressure Relief Valves (PRVs) are historically specified to API Standards. Gas systems and digestors are fitted with PRVs. Flowmeters are installed to monitor gas production and prevent excess pressure in storage tanks and vessels. The gas bag pressures are monitored to ensure it remains within acceptable operating range. If gas in excess of the CHP capacity is generated the flare will operate to avoid over pressure. The gas system is fitted with pressure relief valves in line with gas safety requirements. There are no limit sensors fitted to the tank pressure vacuum relief valves (PVRVs). Logging of the operation of PRVs is not currently undertaken but a review of SCADA data is a means to identify releases. PVRVs have a monthly visual inspection (SW ref. MTM PO0107) and undergo maintainance annually in accordance with SW ref. MTM MF0687. We have reviewed the BAT requirement with our specialist supplier Assentech and have been advised that it is is likely to be considered acceptable based on ongoing discussions. It may be considered an alternative means of compliance and may remain subject to further and wider review with the Agency. Our plan includes the following: Continuation of maintenance regime as above. Procurement of a new leak-rate test rig and development and implemetation of related procedure to complete a periodic leak test. Consideration is that a small leak is more likely to go unoticed and give an unrecorded release. Completion of optical gas imaging activities per LDAR Undertake review of pressure monitoring and SCADA interface to determine SCADA means of logging PVRV operation (comparison of tank and gas system pressures and flows). Our company standards have been updated to reflect the required BS and will include a need in procurement for a leak rate certificate from the manufacturer.
b. | Selection and use of high-integrity equipment | This includes techniques such as: — valves with double packing seals or equally efficient equipment; — high-integrity gaskets (such as spiral wound, ring joints) for critical applications; — pumps/compressors/agitators fitted with mechanical seals instead of packing; — magnetically driven pumps/compressors/agitators; — appropriate service hose access ports, piercing pliers, drill heads, e.g. when degassing WEEE containing VFCs and/or VHCs. | Applicability may be re­ stricter in the case of exist­ ing plants due to operability requirements. | The site was constructed prior to IED, as such we are not able to demonstrate such design considerations were formally considered. The relevant company standards have been updated to ensure any future projects reflect BAT requirements. The equipment installed at site is considered appropriate for use and in line with industry standards. It is not considered cost effective to replace equipment before end of life and there are no specific plans to replace equipment under this BAT.
c. | Corrosion prevention | This includes techniques such as: — appropriate selection of construction materials; — lining or coating of equipment and painting of pipes with corrosion inhibitors. | Generally applicable. | All construction and installations are in line with water Industry specifications and supplemented with Company standards.
d. | Containment, collection and treatment of diffuse emissions | This includes techniques such as: — storing, treating and handling waste and material that may generate diffuse emissions in enclosed buildings and/or enclosed equipment (e.g. conveyor belts); — maintaining the enclosed equipment or buildings under an adequate pressure; — collecting and directing the emissions to an appropriate abatement system (see Section 6.1) via an air extraction system and/or air suction systems close to the emission sources. | The use of enclosed equipment or buildings may be restricted by safety considerations such as the risk of explosion or oxygen depletion. The use of enclosed equipment or buildings may also be constrained by the volume of waste. | IED is considered to have broadened the requirements in relation to this consideration but sites are anticipated to broadly comply with the BAT. Any gaps will be identified through completion of the Air emissions plan which will be provided within 6 months of permit issue. This is part of wider ongoing discussions, specifically with respect to emissions from cake, and is considered to require outcomes from testing to be able to determine appropriate solutions.
e. | Dampening | Dampening potential sources of diffuse dust emissions (e.g. waste storage, traffic areas, and open handling processes) with water or fog. | Generally applicable. | No significant potential dust sources on site.
f. | Maintenance | This includes techniques such as: — ensuring access to potentially leaky equipment; — regularly controlling protective equip­ment such as lamellar curtains, fast-action doors. | Generally applicable. | Maintenance access is considered in design in line with CDM requirements. Some changes to equipment are required to meet BAT and this will be included in design solutions. Where equipment requires specific access arrangements this is to be included in the method statement provided by the contractor completing the work and may require access equipment. Equipment is maintained in line with company requirements and a planned preventative maintenence system is in place for these activities.
g. | Cleaning of waste treat­ment and storage areas | This includes techniques such as regularly cleaning the whole waste treatment area (halls, traffic areas, storage areas, etc.), conveyor belts, equipment and containers. | Generally applicable. | There are general housekeeping and management tasks undertaken and procedures followed by site operatives on a routine basis. Local wash-water hoses are provided to enable prompt clean up, thus minimising any diffuse odour emissions. Some sites have a wheelwash which is used to ensure any cake sludge that might get stuck to the cake wagon wheels is not tracked around the Site or on to the public highway - leading to odour issues
h. | Leak detection and repair (LDAR) programme | See Section 6.2. When emissions of organic compounds are expected, a LDAR programme is set up and implemented using a risk-based approach, considering in particular the design of the plant and the amount and nature of the organic compounds concerned. | Generally applicable. | A site specific leak detection and repair (LDAR) plan is provided as part of the permit application. Some activities were already underway, the implementation of some additional measures has commenced but some activities require procurement of additional equiipment or services. Subject to review comments from the Environment Agency it is anticipated that the LDAR will be fully implemented by the end of 2027 and then continue as business as usual (BAU). The plan acts to improve safety for site operatives, decrease exposure of local sensitive receptors to VOCs, bioaerosols and odour, as well as to reduce product losses.
BAT 15. BAT is to use flaring only for safety reasons or for non-routine operating conditions (e.g. start-ups, shutdowns) by using both of the techniques given below.
Technique |  | Description | Applicability
a. | Correct plant design | This includes the provision of a gas recovery system with sufficient capacity and the use of high-integrity relief valves. | Generally applicable to new plants. A gas recovery system may be retrofitted in existing plants. | There is a gas holder in place to provide storage / balancing of biogas feeding into the CHP. Gas system modelling shows the site is not expected to flare outside of maintenance or emergency scenarios. The available modelling shows flaring would be expected for around 6.5% of the year. The site is considered to have a correctly sized CHP unit for the gas generated. The existing CHP is planned to be retained at this site. However at the time of writing, a combination of equipment issues on site have impacted the gas quality and measured flare hours shows the site has experienced around 20% flaring (of time, pro-rated to annual from Sept 2024-Jan 2025). Work to address the issues is in progress. If the CHP is unavailable (due to downtime or maintenance) the flare will be used to allow the treatment process to safely continue effectively and efficiently. The flare is maintained in accordance with manufacturer's specifications and Southern Water's Maintenance task manual. Testing of the CHP shows emissions are considered compliant. Additional, BAT and BAT-referenced specifications require provision of specific facilities (e.g. monitoring devices, metres and test ports). Work is required to provide the required permanent facilities and will be completed in AMP8. Any work identified as required to ensure the equipment is BAT compliant will be completed in AMP8.
b. | Plant management | This includes balancing the gas system and using advanced process control. | Generally applicable. | The CHP is process controlled through a SCADA system to manage the digestors, gas bag, CHP and Flare together (with associated pumps and valves etc). The gas holder is utilised to balance the gas system flows. In the event the CHP cannot run in an emergency or due to operational issues, biogas will be combusted via an on-site flare stack. The planned asset improvements (along with related IT improvements) will ensure the required data is captured appropriately. Monitoring will be reviewed to ensure the use of PVRVs is minimised and investigated (see BAT 14a). Coordination with emerging PVRV data will allow further review of the overall gas system operation and allow for identification and completion of any required changes to meet BAT.
BAT 16. In order to reduce emissions to air from flares when flaring is unavoidable, BAT is to use both of the techniques given below.
Technique |  | Description | Applicability
a. | Correct design of flaring devices | Optimisation of height and pressure, assistance by steam, air or gas, type of flare tips, etc., to enable smokeless and reliable operation and to ensure the efficient combustion of excess gases. | Generally applicable to new flares. In existing plants, applicability may be restricted, e.g. due to maintenance time availability. | The current flare has been determined to be likely to be non-compliant to BAT for emissions and will be replaced. Testing of the flares has been based on similar flares (make, model) and has informed the overall replacement strategy. Replacement of this flare will be undertaken in AMP8 in line with our asset replacement strategy. Our plans include scope to provide compliant flare stack monitoring and testing for all sites. Additional considerations with respect to flare sizing relate to the optimisation of digestion and CHP sizing, these will be addressed in the relevant plans. Flare stacks installed to company standard ref. MED 4256.
b. | Monitoring and recording as part of flare manage­ ment | This includes continuous monitoring of the quantity of gas sent to flaring. It may include estimations of other parameters (e.g. composition of gas flow, heat content, ratio of assistance, velocity, purge gas flow rate, pollutant emissions (e.g. NOX, CO, hydrocarbons), noise). The recording of flaring events usually includes the duration and number of events and allows for the quantification of emissions and the potential prevention of future flaring events. | Generally applicable. | Flaring run hours monitoring is available at Fullerton however the meter is planned for replacement as part of improvement works. It is recognised that not all BAT-required parameters are currently monitored and the scope includes provision of all required facilities and equipment to meet BAT. The use of this data will also be part of wider improvements in relation to reporting and recording on computerised systems. This may provide opportunities for new trending of asset performance. It is acknowledged that the replacement of the flare would require a permit variation at the appropriate date.

## BAT 17-18
17.8.2018 EN Official Journal of the European Union L 208/59
1.4. Noise and vibrations
BAT 17. In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to set up, implement and regularly review a noise and vibration management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements:
I. a protocol containing appropriate actions and timelines; |  |  |  | SWS have standards and procedures for nuisance management, within the accredited EMS (EMS 240 and 340 respectively). | No specific noise and vibration management plan has been developed and the requirements for this are covered by other procedures. Noise mitigation measures are considered at design stage and look to meet all required legislation. Typical solutions include acoustic enclosures and the utilisation of building are used on some sites, this is reviewed with respect to receptors. During normal operation equipment is routinely checked for any increase in noise or vibration, and maintenance jobs raised and carried out where this is the case. Completion of project work is subject to CDM where noise is considered in project execution planning.
II. a protocol for conducting noise and vibration monitoring; |  |  |  | Vibration forms a part of equipment testing & maintenance and required to be in line with contractors procedures and manufacturers recommendations.
III. a protocol for response to identified noise and vibration events, e.g. complaints; |  |  |  | The accredited EMS has a procedure for nuisance management (EMS 340) and identifies the actions for dealing with and investigating noise complaints.
IV. a noise and vibration reduction programme designed to identify the source(s), to measure/estimate noise and vibration exposure, to characterise the contributions of the sources and to implement prevention and/or reduction measures. |  |  |  | Monitoring and investigation are undertaken on an ad hoc basis when the need arises.
Applicability
The applicability is restricted to cases where a noise or vibration nuisance at sensitive receptors is expected and/or has been substantiated.
BAT 18. In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to use one or a combination of the techniques given below.
Technique |  | Description | Applicability
a. | Appropriate location of equipment and buildings | Noise levels can be reduced by increasing the distance between the emitter and the receiver, by using buildings as noise screens and by relocating building exits or entrances. | For existing plants, the relo­cation of equipment and building exits or entrances may be restricted by a lack of space or excessive costs. | The site was constructed prior to IED, as such we are not able to demonstrate such design considerations were formally considered. Operational procedures for noise and vibration management are covered under the accredited ISO14001:2015 (in particular EMS340 - Procedure for Nuisance Management) and dealt with, and actioned, appropriately especially in respect of noise complaints. All plant and equipment is regularly inspected and maintained to ensure they run effectively and efficiently and are in the best condition they can be to prevent noise and vibration, and staff will raise any maintenance work required. On some sites where equipment is enclosed in buildings, and if an activity is particularly noisy, doors will be closed. Equipment is only operated and maintained by trained and competent staff, who are familiar with the equipment they are working with and are able to identify when issues arise. Many sites have restrictions for noisy operations e.g. deliveries, HGV or tanker movements at certain times and there are speed restrictions and speed calming measures in place to help reduce noise. Where future equipment is to be replaced low-noise emitting equipment will be considered and new plant and equipment will be required to meet specific standards across all areas (not just noise). The plant is existing, and noise is not an issue for the majority of sites due to proxity of the site to sensitive receptors. However, some sites have retro-fitted acoustic barriers or other obstacles for noise attenuation are placed between the noise emitter and the receiving receptor, to specific plant as a precautionary measure or equipment is housed within buildings to minimise any potential noise impacts, if they are close to sensitive receptors.
b. | Operational measures | This includes techniques such as: (i) inspection and maintenance of equip­ ment; (ii) closing of doors and windows of en­ closed areas, if possible; (iii) equipment operation by experienced staff; (iv) avoidance of noisy activities at night, if possible; (v) provisions for noise control during maintenance, traffic, handling and treatment activities. | Generally applicable.
c. | Low-noise equipment | This may include direct drive motors, com­ pressors, pumps and flares.
d. | Noise and vibration control equipment | This includes techniques such as: (i) noise reducers; (ii) acoustic and vibrational insulation of equipment; (iii) enclosure of noisy equipment; (iv) soundproofing of buildings. | Applicability may be restricted by a lack of space (for existing plants).
e. | Noise attenuation | Noise propagation can be reduced by inserting obstacles between emitters and receivers (e.g. protection walls, embankments and buildings). | Applicable only to existing plants, as the design of new plants should make this technique unnecessary. For existing plants, the insertion of obstacles may be restricted by a lack of space. For mechanical treatment in shredders of metal wastes, it is applicable within the constraints associated with the risk of deflagration in shredders.

## BAT 19-20
L 208/60 EN Official Journal of the European Union 17.8.2018
1.5. Emissions to water
BAT 19. In order to optimise water consumption, to reduce the volume of waste water generated and to prevent or, where that is not practicable, to reduce emissions to soil and water, BAT is to use an appropriate combination of the techniques given below.
Technique |  | Description | Applicability
a. | Water management | Water consumption is optimised by using measures which may include: — water saving plans (e.g. establishment of water efficiency objectives, flow diagrams and water mass balances); — optimising the use of washing water (e.g. dry cleaning instead of hosing down, using trigger control on all washing equipment); — reducing the use of water for vacuum generation (e.g. use of liquid ring pumps with high boiling point liquids). | Generally applicable. | Water usage is managed to minimise consumption. Where water does not need to be of a potable / clean standard final effluent is used as a 'wash water ' system on all sites. This supply is used for washing down screens, washing down spills, cleaning tanks, foam suppression and carrier water. Additional metering is required to record and report water usage by process/area per BAT 2 requirements. This will allow identification of further efficiency opportunities (BAT 23) and will be covered in the waste reporting plan.
b. | Water recirculation | Water streams are recirculated within the plant, if necessary after treatment. The degree of recirculation is limited by the water balance of the plant, the content of impurities (e.g. odorous compounds) and/or the characteristics of the water streams (e.g. nutrient content). | Generally applicable. | All STCs recirculate final effluent for washing plant and for a range of non-potable uses. Site drainage directs water landing on impermeable surfaces back to the head of the works to be recirculated through the treatement process.
c. | Impermeable surface | Depending on the risks posed by the waste in terms of soil and/or water contamination, the surface of the whole waste treatment area (e.g. waste reception, handling, storage, treatment and dispatch areas) is made impermeable to the liquids concerned. | Generally applicable. | The site is not BAT compliant. Large areas of the site are not impermeable. i.e. shingle areas. There is broadly no consideration in the orginal site design for secondary containment of tanks. Smaller tanks for specialist chemicals and fuels are typically in double-skinned or collared tanks. Tanks are fitted with level gauges and most with high level and (where applicable) overflow alarms. Typically any over flow will drain to the works return system for full treatment through the WwTW. The permit application documents provide ADBA assesment, spill modelling and an overview of secondary containment plans. The plans remain subject to surveys and design development but have been developed based on CIRIA C736 and the '110% & 25%' rules. A Secondary Containment Plan will be provided to the EA within 6 months of permit issue for agreement. Works will commence at the start of AMP8. Works are targeted to be completed by the end of 2027 but will be completed by the end of AMP8.
d. | Techniques to reduce the likelihood and impact of overflows and failures from tanks and vessels | Depending on the risks posed by the liquids contained in tanks and vessels in terms of soil and/or water contamination, this includes techniques such as: — overflow detectors; — overflow pipes that are directed to a con­ trained drainage system (i.e. the relevant secondary containment or another vessel); — tanks for liquids that are located in a suitable secondary containment; the volume is normally sized to accommodate the loss of containment of the largest tank within the secondary containment; — isolation of tanks, vessels and secondary containment (e.g. closing of valves). | Generally applicable.
e. | Roofing of waste storage and treatment areas | Depending on the risks posed by the waste in terms of soil and/or water contamination, waste is stored and treated in covered areas to prevent contact with rainwater and thus minimise the volume of contaminated run- off water. | Applicability may be constrained when high volumes of waste are stored or treated (e.g. mechanical treatment in shredders of metal waste). | This is most applicable to cake. We have commenced a programme of projects to cover cake bays and seek to continue this through AMP8 WINEP. This will significantly reduce the run-off from cake storage areas and ensure appropriate drainage & containment solutions. Silos are frequently used to mitigate expose of cake. This element of the BAT remains subject to the outcomes of testing for emissions. There is no current plan to enclose cake bays and provide abatement but testing outcomes may determine this requires further review.
f. | Segregation of water streams | Each water stream (e.g. surface run-off water, process water) is collected and treated separately, based on the pollutant content and on the combination of treatment techniques. In particular, uncontaminated waste water streams are segregated from waste water streams that require treatment. | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the water collection system. | The site is existing and does not fully meet BAT. It is recognised that modifications to drainage systems are required to meet BAT. A drainage plan will be provided, this element of BAT is linked to a number of other BAT requirements (secondary containment, sampling/testing) the outcome from those activities will inform the site drainage strategy and and as such we will provide the drainage plan within 12 months of permit issue. The modifications required will be undertaken in AMP8 (in line with secondary containment construction).
g. | Adequate drainage infra­structure | The waste treatment area is connected to drainage infrastructure. Rainwater falling on the treatment and storage areas is collected in the drainage infrastructure along with washing water, occasional spillages, etc. and, depending on the pollutant content, recirculated or sent for further treatment. | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the water drainage system.
h. | Design and maintenance provisions to allow detect­ion and repair of leaks | Regular monitoring for potential leakages is risk-based, and, when necessary, equipment is repaired. The use of underground components is minimised. When underground components are used, and depending on the risks posed by the waste contained in those components in terms of soil and/or water contamination, secondary containment of underground components is put in place. | The use of above-ground components is generally applicable to new plants. It may be limited however by the risk of freezing. The installation of secondary containment may be limited in the case of existing plants. | A large proportion of our on site pipework is below ground and very little has secondary containment or leak detection. A site specific leak detection and repair (LDAR) plan is provided as part of the permit application. Revisions undertaken to company standards will reduce or eliminate new underground pipework on sites (preference being for pipe bridges). It is not anticipated that secondary containment will be retrofitted to existing pipes, the strategy is for improved testing and replacement over time as projects are completed in relation to a given asset/area. It is not anticipated that specific leak detection equipment will be fitted to existing pipework but we will investigate a means of demonstrating no loss of product utilising existing equipment and SCADA (eg. tank gauges, meters, pumps).
i. | Appropriate buffer storage capacity | Appropriate buffer storage capacity is provided for waste water generated during other than normal operating conditions using a risk-based approach (e.g. taking into account the nature of the pollutants, the effects of downstream waste water treatment, and the receiving environment). The discharge of waste water from this buffer storage is only possible after appropriate measures are taken (e.g. monitor, treat, reuse). | Generally applicable to new plants. For existing plants, applicability may be limited by space availability and by the layout of the water collection system. | The interfacing water treatment works is operated by the same company, as such the sites are able to manage flows and capacity on a common operational basis. Site storage capacity is based on company standards and historical norms for process sizing. It is understood that the informaiton provided in the permit application does not include the interfaced works capacity and flows. A Wastewater & Digestate Buffer Storage Plan will be provided within 6 months of permit issue. No IED-driven increase in storage capacity is currently planned but other drivers include plans for additional storm capacity at some sites.
BAT 20. In order to reduce emissions to water, BAT is to treat waste water using an appropriate combination of the techniques given below. |  |  |  | See also response to BAT 7 re. sampling/monitoring which outlines the relevant plan for submission . It is proposed that monitoring will be in line with the requirements of BAT and to be implemented as an improvement condition. The BAT AELs and monitoring frequencies are applicable to treatment of water-based liquid waste and biological treatment of waste, these are outlined in Table 6.1 and Table 6.2 of the BAT assessment
Technique(1) Typical pollutants targeted Applicability
Preliminary and primary treatment, e.g.
a. | Equalisation | All pollutants | Generally applicable.
b. | Neutralisation | Acids, alkalis
c. | Physical separation, e.g. screens, sieves, grit separators, grease separators, oil-water separation or primary settlement tanks | Gross solids, suspended solids, oil/grease |  | All sites have preliminary treatment where grit and screenings will be removed and flow measured for full treatment. Where appropriate excess storm flows will be diverted to the storm tanks. The preliminary process will then be followed by primary settlement tanks where primary sludge is removed and this reduces the organic load onto the biological treatment stage.
Physico-chemical treatment, e.g.
d. | Adsorption | Adsorbable dissolved non-biodegradable or inhibitory pollutants, e.g. hydrocarbons, mercury, AOX | Generally applicable.
e. | Distillation/rectification | Dissolved non-biodegradable or inhibitory pollutants that can be distilled, e.g. some solvents
f. | Precipitation | Precipitable dissolved non-biodegradable or inhibitory pollutants, e.g. metals, phosphorus
g. | Chemical oxidation | Oxidisable dissolved non-biodegradable or inhibitory pollutants, e.g. nitrite, cyanide
h. | Chemical reduction | Reducible dissolved non-biodegradable or inhibitory pollutants, e.g. hexavalent chro­ mium (Cr(VI))
i. | Evaporation | Soluble contaminants
j. | Ion exchange | Ionic dissolved non-biodegradable or inhib­ itory pollutants, e.g. metals
k. | Stripping | Purgeable pollutants, e.g. hydrogen sulphide (H2S), ammonia (NH3), some adsorbable organically bound halogens (AOX), hydro­ carbons
Biological treatment, e.g.
l. | Activated sludge process | Biodegradable organic compounds | Generally applicable. | All STCs have a biological treatment stage that will be either an activated sludge plant or trickling filter.
m. | Membrane bioreactor
Nitrogen removal
n. | Nitrification/denitrification when the treatment in­ cludes a biological treat­ ment | Total nitrogen, ammonia | Nitrification may not be applicable in the case of high chloride concentrations (e.g. above 10 g/l) and when the reduction of the chloride concentration prior to nitri­ fication would not be justi­ fied by the environmental benefits. Nitrification is not applicable when the tem­ perature of the waste water is low (e.g. below 12 °C). | On sites with a specific ammonia / nitrogen consent there will be nitrogen removal stage - either a separate treatment element or a more intensive biological stage.
Solids removal, e.g.
o. | Coagulation and floccula­ tion | Suspended solids and particulate-bound metals | Generally applicable. | Suspended solids will be removed via the primary settlement stage
p. | Sedimentation
q. | Filtration (e.g. sand filtra­ tion, microfiltration, ultra­ filtration)
r. | Flotation
(1) The descriptions of the techniques are given in Section 6.3.
Table 6.1
BAT-associated emission levels (BAT-AELs) for direct discharges to a receiving water body |  |  |  | Each site has its own permitted determinands. Typically they will all include BOD, COD, suspended solids, with certain sites having: Iron Phosphorous Total Nitrogen Ammonia The majority of the listed parameters in Table 6.1 of BAT 20 are not monitored. Refer to each site's discharge permits for more details of the site's specific determinands.
Substance/Parameter | BAT-AEL(1) | Waste treatment process to which the BAT-AEL applies
Total organic carbon (TOC)(2) | 10-60 mg/l | — All waste treatments except treatment of water-based liquid waste
| 10-100 mg/l(3)(4) | — Treatment of water-based liquid waste
Chemical oxygen demand (COD)(2) | 30-180 mg/l | — All waste treatments except treatment of water-based liquid waste
| 30-300 mg/l(3)(4) | — Treatment of water-based liquid waste
Total suspended solids (TSS) | 5-60 mg/l | — All waste treatments
Hydrocarbon oil index (HOI) | 0,5-10 mg/l | — Mechanical treatment in shredders of metal waste — Treatment of WEEE containing VFCs and/or VHCs — Re-refining of waste oil — Physico-chemical treatment of waste with calorific value — Water washing of excavated contaminated soil — Treatment of water-based liquid waste
Total nitrogen (Total N) | 1-25 mg/l(5)(6) | — Biological treatment of waste — Re-refining of waste oil
| 10-60 mg/l(5)(6)(7) | — Treatment of water-based liquid waste
Total phosphorus (Total P) | 0,3-2 mg/l | — Biological treatment of waste
| 1-3 mg/l(4) | — Treatment of water-based liquid waste
Phenol index | 0,05-0,2 mg/l | — Re-refining of waste oil — Physico-chemical treatment of waste with calorific value
| 0,05-0,3 mg/l | — Treatment of water-based liquid waste
Free cyanide (CN-)(8) | 0,02-0,1 mg/l | — Treatment of water-based liquid waste
Adsorbable organically bound halogens (AOX)(8) | 0,2-1 mg/l | — Treatment of water-based liquid waste
Metals and metalloids(8) | Arsenic (expressed as As) | 0,01-0,05 mg/l | — Mechanical treatment in shredders of metal waste — Treatment of WEEE containing VFCs and/or VHCs — Mechanical biological treatment of waste — Re-refining of waste oil — Physico-chemical treatment of waste with calorific value — Physico-chemical treatment of solid and/or pasty waste — Regeneration of spent solvents — Water washing of excavated contaminated soil
| Cadmium (expressed as Cd) | 0,01-0,05 mg/l
| Chromium (expressed as Cr) | 0,01-0,15 mg/l
| Copper (expressed as Cu) | 0,05-0,5 mg/l
| Lead (expressed as Pb) | 0,05-0,1 mg/l(9)
| Nickel (expressed as Ni) | 0,05-0,5 mg/l
| Mercury (expressed as Hg) | 0,5-5 µg/l
| Zinc (expressed as Zn) | 0,1-1 mg/l(10)
| Arsenic (expressed as As) | 0,01-0,1 mg/l | — Treatment of water-based liquid waste
| Cadmium (expressed as Cd) | 0,01-0,1 mg/l
| Chromium (expressed as Cr) | 0,01-0,3 mg/l
| Hexavalent chromium (expressed as Cr(VI)) | 0,01-0,1 mg/l
| Copper (expressed as Cu) | 0,05-0,5 mg/l
| Lead (expressed as Pb) | 0,05-0,3 mg/l
| Nickel (expressed as Ni) | 0,05-1 mg/l
| Mercury (expressed as Hg) | 1-10 µg/l
| Zinc (expressed as Zn) | 0,1-2 mg/l
(1) The averaging periods are defined in the General considerations.
(2) Either the BAT-AEL for COD or the BAT-AEL for TOC applies. TOC monitoring is the preferred option because it does
not rely on the use of very toxic compounds. (3) The upper end of the range may not apply:
— when the abatement efficiency is ≥ 95 % as a rolling yearly average and the waste input shows the following character­ istics: TOC > 2 g/l (or COD > 6 g/l) as a daily average and a high proportion of refractory organic compounds (i.e. which are difficult to biodegrade); or
— in the case of high chloride concentrations (e.g. above 5 g/l in the waste input).
(4) The BAT-AEL may not apply to plants treating drilling muds/cuttings.
(5) The BAT-AEL may not apply when the temperature of the waste water is low (e.g. below 12 °C).
(6) The BAT-AEL may not apply in the case of high chloride concentrations (e.g. above 10 g/l in the waste input).
(7) The BAT-AEL only applies when biological treatment of waste water is used.
(8) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned
in BAT 3.
(9) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(10) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.
The associated monitoring is given in BAT 7.
Table 6.2
BAT-associated emission levels (BAT-AELs) for indirect discharges to a receiving water body
Substance/Parameter |  | BAT-AEL(1)(2) | Waste treatment process to which the BAT-AEL applies | It is accepted that testing is not currently completed to BAT requirements. We are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. We look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, but are to be completed before the end of 2027.
Hydrocarbon oil index (HOI) |  | 0,5-10 mg/l | — Mechanical treatment in shredders of metal waste — Treatment of WEEE containing VFCs and/or VHCs — Re-refining of waste oil — Physico-chemical treatment of waste with calorific value — Water washing of excavated contaminated soil — Treatment of water-based liquid waste
Free cyanide (CN-)(3) |  | 0,02-0,1 mg/l | — Treatment of water-based liquid waste
Adsorbable organically bound halogens (AOX)(3) |  | 0,2-1 mg/l | — Treatment of water-based liquid waste
Metals and me­ talloids(3) | Arsenic (expressed as As) | 0,01-0,05 mg/l | — Mechanical treatment in shredders of metal waste — Treatment of WEEE containing VFCs and/or VHCs — Mechanical biological treatment of waste — Re-refining of waste oil — Physico-chemical treatment of waste with calorific value — Physico-chemical treatment of solid and/or pasty waste — Regeneration of spent solvents — Water washing of excavated contaminated soil
| Cadmium (expressed as Cd) | 0,01-0,05 mg/l
| Chromium (expressed as Cr) | 0,01-0,15 mg/l
| Copper (expressed as Cu) | 0,05-0,5 mg/l
| Lead (expressed as Pb) | 0,05-0,1 mg/l(4)
| Nickel (expressed as Ni) | 0,05-0,5 mg/l
| Mercury (expressed as Hg) | 0,5-5 µg/l
| Zinc (expressed as Zn) | 0,1-1 mg/l(5)
| Arsenic (expressed as As) | 0,01-0,1 mg/l | — Treatment of water-based liquid waste
| Cadmium (expressed as Cd) | 0,01-0,1 mg/l
| Chromium (expressed as Cr) | 0,01-0,3 mg/l
| Hexavalent chromium (expressed as Cr(VI)) | 0,01-0,1 mg/l
| Copper (expressed as Cu) | 0,05-0,5 mg/l
| Lead (expressed as Pb) | 0,05-0,3 mg/l
| Nickel (expressed as Ni) | 0,05-1 mg/l
| Mercury (expressed as Hg) | 1-10 µg/l
| Zinc (expressed as Zn) | 0,1-2 mg/l
(1) The averaging periods are defined in the General considerations.
(2) The BAT-AELs may not apply if the downstream waste water treatment plant abates the pollutants concerned, provided this does not lead to a higher level of pollution in the environment.
(3) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(4) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(5) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.
The associated monitoring is given in BAT 7.

## BAT 21-22
17.8.2018 EN Official Journal of the European Union L 208/67
1.6. Emissions from accidents and incidents
BAT 21. In order to prevent or limit the environmental consequences of accidents and incidents, BAT is to use all of the techniques given below, as part of the accident management plan (see BAT 1). |  |  | An Accident Management plan is provided as part of the permit documentation and outlines the measures in place in relation to this BAT.
Technique |  | Description
a. | Protection measures | These include measures such as: — protection of the plant against malevolent acts; — fire and explosion protection system, containing equipment for pre­vention, detection, and extinction; — accessibility and operability of relevant control equipment in emer­gency situations. | Achieved through the development and implementation of the EMS certified through the ISO 14001: 2015 standard and externally accredited as well as internally audited and reviewed annually to ensure continuing suitability, adequacy, appropriateness and effectiveness. Additional new procedures and updates to relevant existing plans within the system will be undertaken, where necessary, to ensure the requirements and conditions set out within the permit are complied with and gaps filled.
b. | Management of incidental/acci­ dental emissions | Procedures are established and technical provisions are in place to manage (in terms of possible containment) emissions from accidents and incidents such as emissions from spillages, firefighting water, or safety valves. | Management of incidents covered by a number of EMS procedures including: 223 protected species 234 Chemical and Oil storage 260 Pollution prevention 323 Protected species (procedure for mitigation works) 360 pollution prevention procedures 363 Procedure for managing oil spills on site 364 Procedure for managing lime spills on site 367 wastewater breach reporting See 790101_MSD_Main_FUL February 2024 and 790101_MSD_AMP_FUL February 2024.
c. | Incident/accident registration and assessment system | This includes techniques such as: — a log/diary to record all accidents, incidents, changes to procedures and the findings of inspections; — procedures to identify, respond to and learn from such incidents and accidents. | This would be covered within site diaries and other SWS processes such as Trellis, ARM, R&V etc. The EMS has an e-form for reporting of incidents - EMS 413 - non-conformity investigation and corrective/preventative action, 304 - Non-conformance, corrective and preventative action and 388 - waste permit breach and near-miss reporting procedure.
1.7. Material efficiency
BAT 22. In order to use materials efficiently, BAT is to substitute materials with waste.
Description
Waste is used instead of other materials for the treatment of wastes (e.g. waste alkalis or waste acids are used for pH adjustment, fly ashes are used as binders). |  |  | The STCs use a by-product of waste water treatment to create biogas which is used to produced heat and power (renewable energy) for the site. Following the digestion process, the digestate is lime treated (depending requirements) to meet the quality requirement set out in the Safe Sludge Matrix and to comply with the HACCP plan. The treated sludge is recycled to agricultural land. Final effluent produced by the wastewater treatment works will be used on the site wherever possible instead of potable water. Details of waste activities is provided in the Main Supporting Document for the permit
Applicability
Some applicability limitations derive from the risk of contamination posed by the presence of impurities (e.g. heavy metals, POPs, salts, pathogens) in the waste that substitutes other materials. Another limitation is the compatibility of the waste substituting other materials with the waste input (see BAT 2).

## BAT 23
L 208/68 EN Official Journal of the European Union 17.8.2018
1.8. Energy efficiency
BAT 23. In order to use energy efficiently, BAT is to use both of the techniques given below. |  |  | It is acknowedged that we are not in a position to demonstrate compliance with this BAT. Additional metering is required to record and report energy usage by process/area (BAT 2). The output of this will allow development of the required Energy Plan. This BAT is additonally linked to emerging company net zero objectives. As such we will provide an Energy Plan within 12 months of agreement of the related plans and a minimum of 6 months of data from the new metering. Some requirements are met through project-level selection of appropriate equipment.
Technique |  | Description
a. | Energy efficiency plan | An energy efficiency plan entails defining and calculating the specific energy consumption of the activity (or activities), setting key performance indicators on an annual basis (for example, specific energy consumption expressed in kWh/tonne of waste processed) and planning periodic improvement targets and related actions. The plan is adapted to the specificities of the waste treatment in terms of process(es) carried out, waste stream(s) treated, etc. | Each site has a power budget that it is expected to be met. Performance against this budget is monitored monthly at management team meetings. CHP production is similarly budgeted and monitored.
b. | Energy balance record | An energy balance record provides a breakdown of the energy consumption and generation (including exportation) by the type of source (i.e. electricity, gas, conventional liquid fuels, conventional solid fuels, and waste). This includes: (i) information on energy consumption in terms of delivered energy; (ii) information on energy exported from the installation; (iii) energy flow information (e.g. Sankey diagrams or energy balances) showing how the energy is used throughout the process. The energy balance record is adapted to the specificities of the waste treatment in terms of process(es) carried out, waste stream(s) treated, etc. | CHP output and net power consumption will be monitored on a monthly basis and will be compared to the monthly budget.

## BAT 24
L 208/68 EN Official Journal of the European Union 17.8.2018
1.9. Reuse of packaging
BAT 24. In order to reduce the quantity of waste sent for disposal, BAT is to maximise the reuse of packaging, as part of the residues management plan (see BAT 1). | N/A
Description
Packaging (drums, containers, IBCs, pallets, etc.) is reused for containing waste, when it is in good condition and sufficiently clean, depending on a compatibility check between the substances contained (in consecutive uses). If necessary, packaging is sent for appropriate treatment prior to reuse (e.g. reconditioning, cleaning). | Not considered relevant - most chemicals will be designed to be delivered in bulk, thus minimising the requirement for oil/chemical drums, containers, IBC's etc. However, where these are used, they would always be returned to the supplier where possible for cleaning and reuse.
Applicability
Some applicability restrictions derive from the risk of contamination of the waste posed by the reused packaging.

## BAT 33-35
17.8.2018 EN Official Journal of the European Union L 208/73
3. BAT CONCLUSIONS FOR THE BIOLOGICAL TREATMENT OF WASTE
Unless otherwise stated, the BAT conclusions presented in Section 3 apply to the biological treatment of waste, and in addition to the general BAT conclusions in Section 1. The BAT conclusions in Section 3 do not apply to the treatment of water-based liquid waste.
3.1. General BAT conclusions for the biological treatment of waste
3.1.1. Overall environmental performance
BAT 33. In order to reduce odour emissions and to improve the overall environmental performance, BAT is to select the waste input.
Description
The technique consists of carrying out the pre-acceptance, acceptance and sorting of the waste input (see BAT 2) so as to ensure the suitability of the waste input for the waste treatment, e.g. in terms of nutrient balance, moisture or toxic compounds which may reduce the biological activity. | [5 empty] | Covered in BAT2
3.1.2. Emissions to air
BAT 34. In order to reduce channelled emissions to air of dust, organic compounds and odorous compounds, including H2S and NH3, BAT is to use one or a combination of the techniques given below.
Technique |  |  | Description |  |  | Further details are provided in the Odour Management Plan and response to BAT 14.
a. | Adsorption |  | See Section 6.1. |  |  | Not used.
b. | Biofilter |  | See Section 6.1. A pre-treatment of the waste gas before the biofilter (e.g. with a water or acid scrubber) may be needed in the case of a high NH3 content (e.g. 5-40 mg/Nm3) in order to control the media pH and to limit the formation of N2O in the biofilter. Some other odorous compounds (e.g. mercaptans, H2S) can cause acidification of the biofilter media and necessitate the use of a water or alkaline scrubber for pre-treatment of the waste gas before the biofilter. |  |  | Biofilters are used in the OCUs for a large number of the STCs Further information is provided in: Response herein to BAT 12 & 13 OMP Section 4.1
c. | Fabric filter |  | See Section 6.1. The fabric filter is used in the case of mechanical biological treatment of waste. |  |  | Not used.
d. | Thermal oxidation |  | See Section 6.1. |  |  | Not used.
e. | Wet scrubbing |  | See Section 6.1. Water, acid or alkaline scrubbers are used in combination with a biofilter, thermal oxidation or adsorption on activated carbon. |  |  | Wet scrubbing is used in the OCUs for a large number of the STCs Further information is provided in: Response herein to BAT 12 & 13 OMP Section 4.1
Table 6.7
BAT-associated emission levels (BAT-AELs) for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste
Parameter |  | Unit |  | BAT-AEL (Average over the sampling period) | Waste treatment process
NH3 (1)(2) |  | mg/Nm3 |  | 0,3-20 | All biological treatments of waste
Odour concentration(1)(2) |  | ouE/Nm3 |  | 200-1 000
Dust |  | mg/Nm3 |  | 2-5 | Mechanical biological treatment of waste
TVOC |  | mg/Nm3 |  | 5-40(3)
(1) Either the BAT-AEL for NH3 or the BAT-AEL for the odour concentration applies.
(2) This BAT-AEL does not apply to the treatment of waste mainly composed of manure. (3) The lower end of the range can be achieved by using thermal oxidation.
The associated monitoring is given in BAT 8.
3.1.3. Emissions to water and water usage
BAT 35. In order to reduce the generation of waste water and to reduce water usage, BAT is to use all of the techniques given below.
Technique |  |  | Description |  |  | Applicability
a. | Segregation of water streams |  | Leachate seeping from compost piles and windrows is segregated from surface run-off water (see BAT 19f). |  |  | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the water circuits. | Areas of site with the potential for contamination of water (e.g. cake loading area where leachate may be generated) will always drain back to the wastewater treatment works for full treatment, whilst areas that are free from contamination (e.g. roofs, footpaths etc) will drain to the site’s surface water drainage system.
b. | Water recirculation |  | Recirculating process water streams (e.g. from dewatering of liquid digestate in anaerobic processes) or using as much as possible other water streams (e.g. water condensate, rinsing water, surface run-off water). The degree of recirculation is limited by the water balance of the plant, the content of impurities (e.g. heavy metals, salts, pathogens, odorous compounds) and/or the characteristics of the water streams (e.g. nutrient content). |  |  | Generally applicable. | Final effluent generated by the wastewater treatment works wherever possible instead of potable water.is used as a pressure returned effluent as already highlighted in earlier BAT reviews. All wastewater flows from the STC are 'recycled' for full treatment through the WTW.
c. | Minimisation of the genera­tion of leachate |  | Optimising the moisture content of the waste in order to minimise the generation of leachate. |  |  | Generally applicable. | The final product (digested sludge) is dewatered to at least 25%ds as this is deemed the optimal dry solid percentage - balancing power and poly consumption to achieve this target.

## BAT 38
17.8.2018 EN Official Journal of the European Union L 208/75 | Southern Water comments and evidence
3.3. BAT conclusions for the anaerobic treatment of waste
Unless otherwise stated, the BAT conclusions presented in this section apply to the anaerobic treatment of waste, and in addition to the general BAT conclusions for the biological treatment of waste in Section 3.1.
3.3.1. Emissions to air
BAT 38. In order to reduce emissions to air and to improve the overall environmental performance, BAT is to monitor and/or control the key waste and process parameters.
Description
Implementation of a manual and/or automatic monitoring system to: | The anaerobic digestion process is fully automated using key process instrumentation (temperature profiles, feed volume and dry solids, pressure, foam level and biogas production and quality) to effectively monitor and optimise key process parameters to ensure stable digester operation. This includes automatic fail-safe systems which will revert the digester into a safe and stable condition in the event of an incident or episode of instability (e.g. If foam levels reach a critical level the digester feed and mixing systems would be inhibited - requiring an operator to reset). Digesters will contain foam detection instrumentation, and anti-foam and chemical dosing systems to suppress foam in the digester headspace. Anti-foam lance and biogas off-take swan-neck pipework arrangement will minimise the risk of foam getting into biogas system and causing issues downstream. The key controls are HACCP control points - RT and temperature - recorded daily and kept within the SMS system / standard spreadsheet. Other key determinands are also recorded to ensure healthy digestion process. Imports are managed via the weekly production planning process to ensure sites are fed in stable and controlled manner each week. The digesters and auxiliary plant contain instrumentation that will provide early warning of a loss of containment or explosion risk, with appropriate fail-safe operation within the software or hardwired. These include dual-level instrumentation within the digester headspace, as well as level switches in the digester overspill chamber to warn of blockage in the downstream pipework. Digester headspace also contains pressure instrumentation which warns of over pressurisation of the digesters. This is backed up by dual pressure and vacuum relief valves on the digester roof which ventilate to atmosphere. A foam-radar in the digester headspace, combined with an automatic anti-foam dosing system ensures foam does not escape through the biogas off-take pipework, or the PRV's. There is pressure monitoring throughout the biogas system, as well as leak detection on the gas holder and gas detection within buildings to warn of an explosion risk. These systems are linked to fast-acting slam-shut valves which isolate all fuels to combustion plant to remove the risk of a fire or explosion. The flare stack will activate at 90-95% pressure and an alarm will be triggered for flare stack if that fails. There is an alarm system to warn of gas holder at 98% capacity. It has been identified that additional monitoring is required to meet BAT. A plan will be provided within 6 months of permit issue outlining the measures required to meet BAT. This is provisionally to be covered by the Digestate stability plan and monitoring plan but may be more suited to a specific/separate plan.
— ensure a stable digester operation;
— minimise operational difficulties, such as foaming, which may lead to odour emissions;
— provide sufficient early warning of system failures which may lead to a loss of containment and explosions.
This includes monitoring and/or control of key waste and process parameters, e.g.:
— pH and alkalinity of the digester feed;
— digester operating temperature;
— hydraulic and organic loading rates of the digester feed;
— concentration of volatile fatty acids (VFA) and ammonia within the digester and digestate;
— biogas quantity, composition (e.g. H2S) and pressure;
— liquid and foam levels in the digester.

## BAT 52-53
L 208/82 EN Official Journal of the European Union 17.8.2018
5. BAT CONCLUSIONS FOR THE TREATMENT OF WATER-BASED LIQUID WASTE
Unless otherwise stated, the BAT conclusions presented in Section 5 apply to the treatment of water-based liquid waste, and in addition to the general BAT conclusions in Section 1.
5.1. Overall environmental performance
BAT 52. In order to improve the overall environmental performance, BAT is to monitor the waste input as part of the waste pre-acceptance and acceptance procedures (see BAT 2).
Description
Monitoring the waste input, e.g. in terms of: |  |  |  | As per BAT 2 for both sludge import and commercial waste imports
— bioeliminability (e.g. BOD, BOD to COD ratio, Zahn-Wellens test, biological inhibition potential (e.g. inhibition of activated sludge));
— feasibility of emulsion breaking, e.g. by means of laboratory-scale tests.
5.2. Emissions to air
BAT 53. In order to reduce emissions of HCl, NH3 and organic compounds to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below.
Technique |  |  | Description
a. | Adsorption |  | See Section 6.1. | As per BAT 14 and 34
b. | Biofilter
c. | Thermal oxidation
d. | Wet scrubbing
Table 6.10
BAT-associated emission levels (BAT-AELs) for channelled emissions of HCl and TVOC to air from the treatment of water-based liquid waste
Parameter |  | Unit | BAT-AEL(1) (Average over the sampling period)
Hydrogen chloride (HCl) |  | mg/Nm3 | 1-5
TVOC |  |  | 3-20(2)
(1) These BAT-AELs only apply when the substance concerned is identified as relevant in the waste gas stream, based on the inventory mentioned in BAT 3.
(2) The upper end of the range is 45 mg/Nm3 when the emission load is below 0,5 kg/h at the emission point.
The associated monitoring is given in BAT 8.

## BAT 25
17.8.2018 EN Official Journal of the European Union L 208/69
2. BAT CONCLUSIONS FOR THE MECHANICAL TREATMENT OF WASTE
Unless otherwise stated, the BAT conclusions presented in Section 2 apply to the mechanical treatment of waste when it is not combined with biological treatment, and in addition to the general BAT conclusions in Section 1.
2.1. General BAT conclusions for the mechanical treatment of waste
2.1.1. Emissions to air
BAT 25. In order to reduce emissions to air of dust, and of particulate-bound metals, PCDD/F and dioxin-like PCBs, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. | [5 empty] | N/A
Technique |  | Description |  |  | Applicability
a. | Cyclone | See Section 6.1. Cyclones are mainly used as preliminary separators for coarse dust. |  |  | Generally applicable.
b. | Fabric filter | See Section 6.1. |  |  | May not be applicable to ex­ haust air ducts directly con­ nected to the shredder when the effects of deflagration on the fabric filter cannot be mitigated (e.g. by using pressure relief valves).
c. | Wet scrubbing | See Section 6.1. |  |  | Generally applicable.
d. | Water injection into the shredder | The waste to be shredded is damped by injecting water into the shredder. The amount of water injected is regulated in relation to the amount of waste being shredded (which may be monitored via the energy consumed by the shredder motor). The waste gas that contains residual dust is directed to cyclone(s) and/or a wet scrubber. |  |  | Only applicable within the constraints associated with local conditions (e.g. Low temperature, drought).
Table 6.3
BAT-associated emission level (BAT-AEL) for channelled dust emissions to air from the mechanical treatment of waste
Parameter |  |  | Unit | BAT-AEL (Average over the sampling period)
Dust |  |  | mg/Nm3 | 2-5(1)
(1) When a fabric filter is not applicable, the upper end of the range is 10 mg/Nm3.
The associated monitoring is given in BAT 8.

## BAT 26-28
L 208/70 EN Official Journal of the European Union 17.8.2018
2.2. BAT conclusions for the mechanical treatment in shredders of metal waste
Unless otherwise stated, the BAT conclusions presented in this section apply to the mechanical treatment in shredders of metal waste, in addition to BAT 25.
2.2.1. Overall environmental performance
BAT 26. In order to improve the overall environmental performance, and to prevent emissions due to accidents and incidents, BAT is to use BAT 14g and all of the techniques given below: |  |  |  | N/A
(a) implementation of a detailed inspection procedure for baled waste before shredding;
(b) removal of dangerous items from the waste input stream and their safe disposal (e.g. gas cylinders, non-depolluted EoLVs, non-depolluted WEEE, items contaminated with PCBs or mercury, radioactive items);
(c) treatment of containers only when accompanied by a declaration of cleanliness.
2.2.2. Deflagrations
BAT 27. In order to prevent deflagrations and to reduce emissions when deflagrations occur, BAT is to use technique a. and one or both of the techniques b. and c. given below. |  |  |  | N/A
Technique |  | Description | Applicability
a. | Deflagration management plan | This includes: — a deflagration reduction programme designed to identify the source(s), and to implement measures to prevent deflagration occurrences, e.g. inspection of waste input as described in BAT 26a, removal of dangerous items as described in BAT 26b; — a review of historical deflagration incidents and remedies and the dissemination of deflagration knowledge; — a protocol for response to deflagration incidents. | Generally applicable.
b. | Pressure relief dampers | Pressure relief dampers are installed to relieve pressure waves coming from defla­ grations that would otherwise cause major damage and subsequent emissions.
c. | Pre-shredding | Use of a low-speed shredder installed upstream of the main shredder | Generally applicable for new plants, depending on the input material. Applicable for major plant upgrades where a significant number of deflagrations have been substantiated.
2.2.3. Energy efficiency
BAT 28. In order to use energy efficiently, BAT is to keep the shredder feed stable. |  |  |  | N/A
Description
The shredder feed is equalised by avoiding disruption or overload of the waste feed which would lead to unwanted shutdowns and start-ups of the shredder.

## BAT 29-30
17.8.2018 EN Official Journal of the European Union L 208/71
2.3. BAT conclusions for the treatment of WEEE containing VFCs and/or VHCs
Unless otherwise stated, the BAT conclusions presented in this section apply to the treatment of WEEE containing VFCs and/or VHCs, in addition to BAT 25.
2.3.1. Emissions to air
BAT 29. In order to prevent or, where that is not practicable, to reduce emissions of organic compounds to air, BAT is to apply BAT 14d, BAT 14h and to use technique a. and one or both of the techniques b. and c. given below. |  |  |  |  | N/A
Technique |  |  | Description
a. | Optimised removal and cap­ ture of refrigerants and oils |  | All refrigerants and oils are removed from the WEEE containing VFCs and/or VHCs and captured by a vacuum suction system (e.g. achieving refrigerant removal of at least 90 %). Refrigerants are separated from oils and the oils are degassed. The amount of oil remaining in the compressor is reduced to a mini­ mum (so that the compressor does not drip).
b. | Cryogenic condensation |  | Waste gas containing organic compounds such as VFCs/VHCs is sent to a cryogenic condensation unit where they are liquefied (see description in Section 6.1). The liquefied gas is stored in pressurised vessels for further treatment.
c. | Adsorption |  | Waste gas containing organic compounds such as VFCs/VHCs is led into adsorption systems (see description in Section 6.1). The spent activated carbon is regenerated by means of heated air pumped into the filter to desorb the organic compounds. Subsequently, the regeneration waste gas is compressed and cooled in order to liquefy the organic compounds (in some cases by cryogenic condensation). The liquefied gas is then stored in pressurised vessels. The remaining waste gas from the compression stage is usually led back into the adsorption system in order to minimise VFC/VHC emissions.
Table 6.4
BAT-associated emission levels (BAT-AELs) for channelled TVOC and CFC emissions to air from the treatment of WEEE containing VFCs and/or VHCs
Parameter |  | Unit |  | BAT-AEL (Average over the sampling period)
TVOC |  | mg/Nm3 |  | 3-15
CFCs |  | mg/Nm3 |  | 0,5-10
The associated monitoring is given in BAT 8.
2.3.2. Explosions
BAT 30. In order to prevent emissions due to explosions when treating WEEE containing VFCs and/or VHCs, BAT is to use either of the techniques given below. |  |  |  |  | N/A
Technique |  |  | Description
a. | Inert atmosphere |  | By injecting inert gas (e.g. nitrogen), the oxygen concentration in enclosed equipment (e.g. in enclosed shredders, crushers, dust and foam collectors) is reduced (e.g. to 4 vol-%).
b. | Forced ventilation |  | By using forced ventilation, the hydrocarbon concentration in enclosed equipment (e.g. in enclosed shredders, crushers, dust and foam collectors) is reduced to < 25 % of the lower explosive limit.

## BAT 31-32
L 208/72 EN Official Journal of the European Union 17.8.2018
2.4. BAT conclusions for the mechanical treatment of waste with calorific value
In addition to BAT 25, the BAT conclusions presented in this section apply to the mechanical treatment of waste with calorific value covered by points 5.3(a)(iii) and 5.3(b)(ii) of Annex I to Directive 2010/75/EU.
2.4.1. Emissions to air
BAT 31. In order to reduce emissions to air of organic compounds, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  |  |  | N/A
Technique |  |  | Description
a. | Adsorption |  | See Section 6.1.
b. | Biofilter
c. | Thermal oxidation
d. | Wet scrubbing
Table 6.5
BAT-associated emission level (BAT-AEL) for channelled TVOC emissions to air from the mechanical treatment of waste with calorific value
Parameter |  | Unit |  | BAT-AEL (Average over the sampling period)
TVOC |  | mg/Nm3 |  | 10-30(1)
(1) The BAT-AEL only applies when organic compounds are identified as relevant in the waste gas stream, based on the inventory mentioned in BAT 3.
The associated monitoring is given in BAT 8.
2.5. BAT conclusions for the mechanical treatment of WEEE containing mercury
Unless otherwise stated, the BAT conclusions presented in this section apply to the mechanical treatment of WEEE containing mercury, in addition to BAT 25.
2.5.1. Emissions to air
BAT 32. In order to reduce mercury emissions to air, BAT is to collect mercury emissions at source, to send them to abatement and to carry out adequate monitoring. |  |  |  |  | N/A
Description
This includes all of the following measures:
— equipment used to treat WEEE containing mercury is enclosed, under negative pressure and connected to a local exhaust ventilation (LEV) system;
— waste gas from the processes is treated by dedusting techniques such as cyclones, fabric filters, and HEPA filters, followed by adsorption on activated carbon (see Section 6.1);
— the efficiency of the waste gas treatment is monitored;
— mercury levels in the treatment and storage areas are measured frequently (e.g. once every week) to detect potential mercury leaks.
Table 6.6
BAT-associated emission level (BAT-AEL) for channelled mercury emissions to air from the mechanical treatment of WEEE containing mercury
Parameter |  | Unit |  | BAT-AEL (Average over the sampling period)
Mercury (Hg) |  | µg/Nm3 |  | 2-7
The associated monitoring is given in BAT 8.

## BAT 36-37
17.8.2018 EN Official Journal of the European Union L 208/75
3.2. BAT conclusions for the aerobic treatment of waste
Unless otherwise stated, the BAT conclusions presented in this section apply to the aerobic treatment of waste, and in addition to the general BAT conclusions for the biological treatment of waste in Section 3.1.
3.2.1. Overall environmental performance
BAT 36. In order to reduce emissions to air and to improve the overall environmental performance, BAT is to monitor and/or control the key waste and process parameters. |  |  |  | N/A
Description
Monitoring and/or control of key waste and process parameters, including:
— waste input characteristics (e.g. C to N ratio, particle size);
— temperature and moisture content at different points in the windrow;
— aeration of the windrow (e.g. via the windrow turning frequency, O2 and/or CO2 concentration in the windrow, temperature of air streams in the case of forced aeration);
— windrow porosity, height and width.
Applicability
Monitoring of the moisture content in the windrow is not applicable to enclosed processes when health and/or safety issues have been identified. In that case, the moisture content can be monitored before loading the waste into the enclosed composting stage and adjusted when it exits the enclosed composting stage.
3.2.2. Odour and diffuse emissions to air
BAT 37. In order to reduce diffuse emissions to air of dust, odour and bioaerosols from open-air treatment steps, BAT is to use one or both of the techniques given below. |  |  |  | N/A
Technique |  | Description | Applicability
a. | Use of semipermeable membrane covers | Active composting windrows are covered by semipermeable membranes. | Generally applicable.
b. | Adaptation of operations to the meteorological condi­ tions | This includes techniques such as the following: — Taking into account weather conditions and forecasts when undertaking major outdoor process activities. For instance, avoiding formation or turning of windrows or piles, screening or shredding in the case of adverse meteorological conditions in terms of emissions dispersion (e.g. the wind speed is too low or too high, or the wind blows in the direction of sensitive receptors). — Orientating windrows, so that the smallest possible area of composting mass is exposed to the prevailing wind, to reduce the dispersion of pollutants from the windrow surface. The windrows and piles are preferably located at the lowest elevation within the overall site layout. | Generally applicable.

## BAT 39
L 208/76 EN Official Journal of the European Union 17.8.2018
3.4. BAT conclusions for the mechanical biological treatment (MBT) of waste
Unless otherwise stated, the BAT conclusions presented in this section apply to MBT, and in addition to the general BAT conclusions for the biological treatment of waste in Section 3.1.
The BAT conclusions for the aerobic treatment (Section 3.2) and anaerobic treatment (Section 3.3) of waste apply, when relevant, to the mechanical biological treatment of waste.
3.4.1. Emissions to air
BAT 39. In order to reduce emissions to air, BAT is to use both of the techniques given below. |  |  |  | N/A
Technique |  | Description | Applicability
a. | Segregation of the waste gas streams | Splitting of the total waste gas stream into waste gas streams with a high pollutant content and waste gas streams with a low pollutant content, as identified in the inventory mentioned in BAT 3. | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the air circuits.
b. | Recirculation of waste gas | Recirculation of waste gas with a low pollutant content in the biological process followed by waste gas treatment adapted to the concentration of pollutants (see BAT 34). The use of waste gas in the biological process may be limited by the waste gas temperature and/or the pollutant content. It may be necessary to condense the water vapour contained in the waste gas before reuse. In this case, cooling is necessary, and the condensed water is recirculated when possible (see BAT 35) or treated before discharge.

## BAT 40-41
17.8.2018 EN Official Journal of the European Union L 208/77
4. BAT CONCLUSIONS FOR THE PHYSICO-CHEMICAL TREATMENT OF WASTE
Unless otherwise stated, the BAT conclusions presented in Section 4 apply to the physico-chemical treatment of waste, and in addition to the general BAT conclusions in Section 1.
4.1. BAT conclusions for the physico-chemical treatment of solid and/or pasty waste
4.1.1. Overall environmental performance
BAT 40. In order to improve the overall environmental performance, BAT is to monitor the waste input as part of the waste pre-acceptance and acceptance procedures (see BAT 2). |  |  |  |  | N/A
Description
Monitoring the waste input, e.g. in terms of:
— content of organics, oxidising agents, metals (e.g. mercury), salts, odorous compounds;
— H2 formation potential upon mixing of flue-gas treatment residues, e.g. fly ashes, with water.
4.1.2. Emissions to air
BAT 41. In order to reduce emissions of dust, organic compounds and NH3 to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  |  |  | N/A
Technique |  |  | Description
a. | Adsorption |  | See Section 6.1.
b. | Biofilter
c. | Fabric filter
d. | Wet scrubbing
Table 6.8
BAT-associated emission level (BAT-AEL) for channelled emissions of dust to air from the physico- chemical treatment of solid and/or pasty waste
Parameter |  | Unit |  | BAT-AEL (Average over the sampling period)
Dust |  | mg/Nm3 |  | 2-5
The associated monitoring is given in BAT 8.

## BAT 42-45
L 208/78 EN Official Journal of the European Union 17.8.2018
4.2. BAT conclusions for the re-refining of waste oil
4.2.1. Overall environmental performance
BAT 42. In order to improve the overall environmental performance, BAT is to monitor the waste input as part of the waste pre-acceptance and acceptance procedures (see BAT 2). |  |  | N/A
Description
Monitoring of the waste input in terms of content of chlorinated compounds (e.g. chlorinated solvents or PCBs).
BAT 43. In order to reduce the quantity of waste sent for disposal, BAT is to use one or both of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Material recovery | Using the organic residues from vacuum distillation, solvent extraction, thin film evaporators, etc. in asphalt products, etc.
b. | Energy recovery | Using the organic residues from vacuum distillation, solvent extraction, thin film evaporators, etc. to recover energy.
4.2.2. Emissions to air
BAT 44. In order to reduce emissions of organic compounds to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Adsorption | See Section 6.1.
b. | Thermal oxidation | See Section 6.1. This includes when the waste gas is sent to a process furnace or a boiler.
c. | Wet scrubbing | See Section 6.1.
The BAT-AEL set in Section 4.5 applies.
The associated monitoring is given in BAT 8.
4.3. BAT conclusions for the physico-chemical treatment of waste with calorific value
4.3.1. Emissions to air
BAT 45. In order to reduce emissions of organic compounds to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Adsorption | See Section 6.1
b. | Cryogenic condensation
c. | Thermal oxidation
d. | Wet scrubbing
The BAT-AEL set in Section 4.5 applies.
The associated monitoring is given in BAT 8.

## BAT 46-47
17.8.2018 EN Official Journal of the European Union L 208/79
4.4. BAT conclusions for the regeneration of spent solvents
4.4.1. Overall environmental performance
BAT 46. In order to improve the overall environmental performance of the regeneration of spent solvents, BAT is to use one or both of the techniques given below. |  |  |  |  | N/A
Technique |  | Description | Applicability
a. | Material recovery | Solvents are recovered from the distillation residues by evaporation. | Applicability may be restricted when the energy demand is excessive with regards to the quantity of solvent recovered.
b. | Energy recovery | The residues from distillation are used to recover energy. | Generally applicable.
4.4.2. Emissions to air
BAT 47. In order to reduce emissions of organic compounds to air, BAT is to apply BAT 14d and to use a combination of the techniques given below. |  |  |  |  | N/A
Technique |  | Description | Applicability
a. | Recirculation of process off-gases in a steam boiler | The process off-gases from the condensers are sent to the steam boiler supplying the plant. | May not be applicable to the treatment of halogenated solvent wastes, in order to avoid generating and emitting PCBs and/or PCDD/F.
b. | Adsorption | See Section 6.1. | There may be limitations to the applicability of the technique due to safety reasons (e.g. activated carbon beds tend to self-ignite when loaded with ketones).
c. | Thermal oxidation | See Section 6.1. | May not be applicable to the treatment of halogenated solvent wastes, in order to avoid generating and emitting PCBs and/or PCDD/F.
d. | Condensation or cryogenic condensation | See Section 6.1. | Generally applicable.
e. | Wet scrubbing | See Section 6.1. | Generally applicable.
The BAT-AEL set in Section 4.5 applies.
The associated monitoring is given in BAT 8.
4.5. BAT-AEL for emissions of organic compounds to air from the re-refining of waste oil, the physico- chemical treatment of waste with calorific value and the regeneration of spent solvents
Table 6.9
BAT-associated emission level (BAT-AEL) for channelled emissions of TVOC to air from the re-refining of waste oil, the physico-chemical treatment of waste with calorific value and the regeneration of spent solvents
Parameter |  |  | Unit | BAT-AEL(1) (Average over the sampling period)
TVOC |  |  | mg/Nm3 | 5-30
(1) The BAT-AEL does not apply when the emission load is below 2 kg/h at the emission point provided that no CMR substances are identified as relevant in the waste gas stream, based on the inventory mentioned in BAT 3.

## BAT 48
L 208/80 EN Official Journal of the European Union 17.8.2018
4.6. BAT conclusions for the thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil
4.6.1. Overall environmental performance
BAT 48. In order to improve the overall environmental performance of the thermal treatment of spent activated carbon, waste catalysts and excavated contaminated soil, BAT is to use all of the techniques given below. |  |  |  | N/A
Technique |  | Description | Applicability
a. | Heat recovery from the fur­ nace off-gas | Recovered heat may be used, for example, for preheating of combustion air or for the generation of steam, which is also used in the reactivation of the spent activated carbon. | Generally applicable.
b. | Indirectly fired furnace | An indirectly fired furnace is used to avoid contact between the contents of the furnace and the flue-gases from the burner(s). | Indirectly fired furnaces are normally constructed with a metal tube and applicability may be restricted due to corrosion problems. There may be also economic restrictions for retrofitting existing plants.
c. | Process-integrated techniques to reduce emissions to air | This includes techniques such as: — control of the furnace temperature and of the rotation speed of the rotary furnace; — choice of fuel; — use of a sealed furnace or operation of the furnace at a reduced pressure to avoid diffuse emissions to air. | Generally applicable.

## BAT 49-51
17.8.2018 EN Official Journal of the European Union L 208/81
4.6.2. Emissions to air
BAT 49. In order to reduce emissions of HCl, HF, dust and organic compounds to air, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Cyclone | See Section 6.1. The technique is used in combination with further abatement techniques.
b. | Electrostatic precipitator (ESP) | See Section 6.1.
c. | Fabric filter
d. | Wet scrubbing
e. | Adsorption
f. | Condensation
g. | Thermal oxidation(1)
(1) Thermal oxidation is carried out with a minimum temperature of 1 100 °C and a two-second residence time for the regeneration of activated carbon used in industrial applications where refractory halogenated or other thermally resistant substances are likely to be present. In the case of activated carbon used for potable water- and food-grade applications, an afterburner with a minimum heating temperature of 850 °C and a two-second residence time is sufficient (see Section 6.1).
The associated monitoring is given in BAT 8.
4.7. BAT conclusions for the water washing of excavated contaminated soil
4.7.1. Emissions to air
BAT 50. In order to reduce emissions of dust and organic compounds to air from the storage, handling, and washing steps, BAT is to apply BAT 14d and to use one or a combination of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Adsorption | See Section 6.1.
b. | Fabric filter
c. | Wet scrubbing
The associated monitoring is given in BAT 8.
4.8. BAT conclusions for the decontamination of equipment containing PCBs
4.8.1. Overall environmental performance
BAT 51. In order to improve the overall environmental performance and to reduce channelled emissions of PCBs and organic compounds to air, BAT is to use all of the techniques given below. |  |  | N/A
Technique |  | Description
a. | Coating of the storage and treatment areas | This includes techniques such as: — resin coating applied to the concrete floor of the whole storage and treatment area.
b. | Implementation of staff access rules to prevent dispersion of contamination | This includes techniques such as: — access points to storage and treatment areas are locked; — special qualification is required to access the area where the con­ taminated equipment is stored and handled; — separate ‘clean’ and ‘dirty’ cloakrooms to put on/remove individual protective outfit.
c. | Optimised equipment cleaning and drainage | This includes techniques such as: — external surfaces of the contaminated equipment are cleaned with anionic detergent; — emptying of the equipment with a pump or under vacuum instead of gravity emptying; — procedures are defined and used for filling, emptying and (dis)con­ necting the vacuum vessel; — a long period of drainage (at least 12 hours) is ensured to avoid any dripping of contaminated liquid during further treatment operations, after the separation of the core from the casing of an electrical transformer.
d. | Control and monitoring of emissions to air | This includes techniques such as: — the air of the decontamination area is collected and treated with activated carbon filters; — the exhaust of the vacuum pump mentioned in technique c. above is connected to an end-of-pipe abatement system (e.g. a high-temperature incinerator, thermal oxidation or adsorption on activated carbon); — the channelled emissions are monitored (see BAT 8); — the potential atmospheric deposition of PCBs is monitored (e.g. through physico-chemical measurements or biomonitoring).
e. | Disposal of waste treatment residues | This includes techniques such as: — porous, contaminated parts of the electrical transformer (wood and paper) are sent to high-temperature incineration; — PCBs in the oils are destroyed (e.g. dechlorination, hydrogenation, solvated electron processes, high-temperature incineration).
f. | Recovery of solvent when solvent washing is used | Organic solvent is collected and distilled to be reused in the process.
The associated monitoring is given in BAT 8.

## Additional techniques descrips
L 208/84 EN Official Journal of the European Union 17.8.2018
6. DESCRIPTION OF TECHNIQUES
6.1. Channelled emissions to air
Technique | Typical pollutant(s) abated | Description
Adsorption | Mercury, volatile organic com­ pounds, hydrogen sulphide, odorous compounds | Adsorption is a heterogeneous reaction in which gas molecules are retained on a solid or liquid surface that prefers specific compounds to others and thus removes them from effluent streams. When the surface has adsorbed as much as it can, the adsorbent is replaced or the adsorbed content is desorbed as part of the regeneration of the adsorbent. When desorbed, the contaminants are usually at a higher concentration and can either be recovered or disposed of. The most common adsorbent is granular activated carbon.
Biofilter | Ammonia, hydrogen sulphide, volatile organic compounds, odorous compounds | The waste gas stream is passed through a bed of organic material (such as peat, heather, compost, root, tree bark, softwood and different combinations) or some inert material (such as clay, activated carbon, and polyurethane), where it is biologically oxidised by naturally occurring microorganisms into carbon dioxide, water, inorganic salts and biomass. A biofilter is designed considering the type(s) of waste input. An appropriate bed material, e.g. in terms of water retention capacity, bulk density, porosity, structural integrity, is selected. Also important are an appropriate height and surface area of the filter bed. The biofilter is connected to a suitable ventilation and air circulation system in order to ensure a uniform air distribution through the bed and a sufficient residence time of the waste gas inside the bed.
Condensation and cryogenic condensation | Volatile organic compounds | Condensation is a technique that eliminates solvent vapours from a waste gas stream by reducing its temperature below its dew point. For cryogenic condensation, the operating temperature can be down to – 120 °C, but in practice it is often between – 40 °C and – 80 °C in the condensation device. Cryogenic condensation can cope with all VOCs and volatile inorganic pollutants, irrespective of their individual vapour pressures. The low temperatures applied allow for very high condensation efficiencies which make it well-suited as a final VOC emission control technique.
Cyclone | Dust | Cyclone filters are used to remove heavier particulates, which ‘fall out’ as the waste gases are forced into a rotating motion before they leave the separator. Cyclones are used to control particulate material, primarily PM10.
Electrostatic precipitator (ESP) | Dust | Electrostatic precipitators operate such that particles are charged and separated under the influence of an electrical field. Electrostatic precipitators are capable of operating under a wide range of conditions. In a dry ESP, the collected material is mechanically removed (e.g. by shaking, vibration, compressed air), while in a wet ESP it is flushed with a suitable liquid, usually water.
Fabric filter | Dust | Fabric filters, often referred to as bag filters, are constructed from porous woven or felted fabric through which gases are passed to remove particles. The use of a fabric filter requires the selection of a fabric suitable for the characteristics of the waste gas and the maximum operating temperature.
HEPA filter | Dust | HEPA filters (high-efficiency particle air filters) are absolute filters. The filter medium consists of paper or matted glass fibre with a high packing density. The waste gas stream is passed through the filter medium, where particulate matter is collected.
Thermal oxidation | Volatile organic compounds | The oxidation of combustible gases and odorants in a waste gas stream by heating the mixture of contaminants with air or oxygen to above its auto-ignition point in a combustion chamber and maintaining it at a high temperature long enough to complete its combustion to carbon dioxide and water.
Wet scrubbing | Dust, volatile organic compounds, gaseous acidic compounds (alkaline scrubber), gaseous alkaline compounds (acid scrubber) | The removal of gaseous or particulate pollutants from a gas stream via mass transfer to a liquid solvent, often water or an aqueous solution. It may involve a chemical reaction (e.g. in an acid or alkaline scrubber). In some cases, the compounds may be recovered from the solvent.
6.2. Diffuse emissions of organic compounds to air
Leak detection and repair (LDAR) programme | Volatile organic compounds | A structured approach to reduce fugitive emissions of organic compounds by detection and subsequent repair or replacement of leaking components. Currently, sniffing (described by EN 15446) and optical gas imaging methods are available for the identification of leaks. Sniffing method: The first step is the detection using hand-held organic compound analysers measuring the concentration adjacent to the equipment (e.g. using flame ionisation or photoionisation). The second step consists of enclosing the component in an impermeable bag to carry out a direct measurement at the source of the emission. This second step is sometimes replaced by mathematical correlation curves derived from statistical results obtained from a large number of previous measurements made on similar components. Optical gas imaging methods: Optical imaging uses small lightweight hand-held cameras which enable the visualisation of gas leaks in real time, so that they appear as ‘smoke’ on a video recorder together with the normal image of the component concerned, to easily and rapidly locate significant organic compound leaks. Active systems produce an image with a backscattered infrared laser light reflected on the component and its surroundings. Passive systems are based on the natural infrared radiation of the equipment and its surroundings.
Measurement of diffuse VOC emissions | Volatile organic compounds | Sniffing and optical gas imaging methods are described under leak detection and repair proramme. Full screening and quantification of emissions from the installation can be undertaken with an appropriate combination of complementary methods, e.g. Solar occultation flux (SOF) or Differential absorption LIDAR (DIAL) campaigns. These results can be used for trend evaluation over time, cross-checking and updating/validation of the ongoing LDAR programme. Solar occultation flux (SOF): The technique is based on the recording and spectrometric Fourier Transform analysis of a broadband infra­red or ultraviolet/visible sunlight spectrum along a given geographical itinerary, crossing the wind direction and cutting through VOC plumes. Differential absorption LIDAR (DIAL): This is a laser-based technique using differential absorption LIDAR (light detection and ranging), which is the optical analogue of radio wave-based RADAR. The technique relies on the backscattering of laser beam pulses by atmospheric aerosols, and the analysis of the spectral properties of the returned light collected with a telescope.
6.3. Emissions to water
Technique | Typical pollutant(s) targeted | Description
Activated sludge process | Biodegradable organic compounds | The biological oxidation of dissolved organic pollutants with oxygen using the metabolism of microorganisms. In the presence of dissolved oxygen (injected as air or pure oxygen), the organic components are transformed into carbon dioxide, water or other metabolites and biomass (i.e. the activated sludge). The microorganisms are maintained in suspension in the waste water and the whole mixture is mechanically aerated. The activated sludge mixture is sent to a separation facility from where the sludge is recycled to the aeration tank.
Adsorption | Adsorbable dissolved non-biodegradable or inhibitory pollutants, e.g. hydrocarbons, mercury, AOX | Separation method in which compounds (i.e. pollutants) in a fluid (i.e. wastewater) are retained on a solid surface (typically activated carbon).
Chemical oxidation | Oxidisable dissolved non-biodegradable or inhibitory pollutants, e.g. nitrite, cyanide | Organic compounds are oxidised to less harmful and more easily biodegradable compounds. Techniques include wet oxidation or oxidation with ozone or hydrogen peroxide, optionally supported by catalysts or UV radiation. Chemical oxidation is also used to degrade organic compounds causing odour, taste and colour and for disinfection purposes.
Chemical reduction | Reducible dissolved non-biodegradable or inhibitory pollutants, e.g. hexavalent chromium (Cr(VI)) | Chemical reduction is the conversion of pollutants by chemical reducing agents into similar but less harmful or hazardous compounds.
Coagulation and flocculation | Suspended solids and particulate-bound metals | Coagulation and flocculation are used to separate suspended solids from waste water and are often carried out in successive steps. Coagulation is carried out by adding coagulants with charges opposite to those of the suspended solids. Flocculation is carried out by adding polymers, so that collisions of microfloc particles cause them to bond to produce larger flocs. The flocs formed are subsequently separated by sedimentation, air flotation or filtration.
Distillation/rectification | Dissolved non-biodegradable or inhibitory pollutants that can be distilled, e.g. some solvents | Distillation is a technique to separate compounds with different boiling points by partial evaporation and recondensation. Waste water distillation is the removal of low-boiling contaminants from waste water by transferring them into the vapour phase. Distillation is carried out in columns, equipped with plates or packing material, and a downstream condenser.
Equalisation | All pollutants | Balancing of flows and pollutant loads by using tanks or other management techniques.
Evaporation | Soluble pollutants | The use of distillation (see above) to concentrate aqueous solutions of high-boiling substances for further use, processing or disposal (e.g. waste water incineration) by transferring water to the vapour phase. It is typically carried out in multi-stage units with increasing vacuum, to reduce the energy demand. The water vapours are condensed, to be reused or discharged as waste water.
Filtration | Suspended solids and particulate-bound metals | The separation of solids from waste water by passing them through a porous medium, e.g. sand filtration, microfiltration and ultrafiltration.
Flotation |  | The separation of solid or liquid particles from waste water by attaching them to fine gas bubbles, usually air. The buoyant particles accumulate at the water surface and are collected with skimmers.
Ion exchange | Ionic dissolved non-biodegradable or inhibitory pollutants, e.g. metals | The retention of undesired or hazardous ionic constituents of waste water and their replacement by more acceptable ions using an ion exchange resin. The pollutants are temporarily retained and afterwards released into a regeneration or backwashing liquid.
Membrane bioreactor | Biodegradable organic compounds | A combination of activated sludge treatment and membrane filtration. Two variants are used: a) an external recirculation loop between the activated sludge tank and the membrane module; and b) immersion of the membrane module in the aerated activated sludge tank, where the effluent is filtered through a hollow fibre membrane, the biomass remaining in the tank.
Membrane filtration | Suspended solids and particulate-bound metals | Microfiltration (MF) and ultrafiltration (UF) are membrane filtration processes that retain and concentrate, on one side of the membrane, pollutants such as suspended particles and colloidal particles contained in waste waters.
Neutralisation | Acids, alkalis | The adjustment of the pH of waste water to a neutral level (approximately 7) by the addition of chemicals. Sodium hydroxide (NaOH) or calcium hydroxide (Ca(OH)2) may be used to increase the pH, whereas sulphuric acid (H2SO4), hydrochloric acid (HCl) or carbon dioxide (CO2) may be used to decrease the pH. The precipitation of some pollutants may occur during neutralisation.
Nitrification/denitrification | Total nitrogen, ammonia | A two-step process that is typically incorporated into biological waste water treatment plants. The first step is aerobic nitrification where micro­organisms oxidise ammonium (NH4+) to the intermediate nitrite (NO2-), which is then further oxidised to nitrate (NO3-). In the subsequent anoxic denitrification step, microorganisms chemically reduce nitrate to nitrogen gas.
Oil-water separation | Oil/grease | The separation of oil and water and subsequent oil removal by gravity separation of free oil, using separation equipment or emulsion breaking (using emulsion breaking chemicals such as metal salts, mineral acids, adsorbents and organic polymers).
Sedimentation | Suspended solids and particu­ late-bound metals | The separation of suspended particles by gravitational settling.
Precipitation | Precipitable dissolved non-biodegradable or inhibitory pollutants, e.g. metals, phosphorus | The conversion of dissolved pollutants into in­soluble compounds by adding precipitants. The solid precipitates formed are subsequently separated by sedimentation, air flotation or filtration.
Stripping | Purgeable pollutants, e.g. hydrogen sulphide (H2S), ammonia (NH3), some adsorbable organically bound halogens (AOX), hydrocarbons | The removal of purgeable pollutants from the aqueous phase by a gaseous phase (e.g. steam, nitrogen or air) that is passed through the liquid. They are subsequently recovered (e.g. by condensation) for further use or disposal. The removal efficiency may be enhanced by increasing the temperature or reducing the pressure.
6.4. Sorting techniques
Technique | Description
Air classification | Air classification (or air separation, or aeraulic separation) is a process of approximate sizing of dry mixtures of different particle sizes into groups or grades at cut points ranging from 10 mesh to sub-mesh sizes. Air classifiers (also called windsifters) complement screens in applications requiring cut points below commercial screen sizes, and supplement sieves and screens for coarser cuts where the special advantages of air classification warrant it.
All-metal separator | Metals (ferrous and non-ferrous) are sorted by means of a detection coil, in which the magnetic field is influenced by metal particles, linked to a processor that controls the air jet for ejecting the materials that have been detected.
Electromagnetic separation of non-fer­ rous metals | Non-ferrous metals are sorted by means of eddy current separators. An eddy current is induced by a series of rare earth magnetic or ceramic rotors at the head of a conveyor that spins at high speed independently of the conveyor. This process induces temporary magnetic forces in non-magnetic metals of the same polarity as the rotor, causing the metals to be repelled away and then separated from the other feedstock.
Manual separation | Material is manually separated by means of visual examination by staff on a picking line or on the floor, either to selectively remove a target material from a general waste stream or to remove contamination from an output stream to increase purity. This technique generally targets re­ cyclables (glass, plastic, etc.) and any contaminants, hazardous materials and oversized materials such as WEEE.
Magnetic separation | Ferrous metals are sorted by means of a magnet which attracts ferrous metal materials. This can be carried out, for example, by an overband magnetic separator or a magnetic drum.
Near-infrared spectroscopy (NIRS) | Materials are sorted by means of a near-infrared sensor which scans the whole width of the belt conveyor and transmits the characteristic spec­ tra of the different materials to a data processor which controls an air jet for ejecting the materials that have been detected. Generally NIRS is not suitable for sorting black materials.
Sink-float tanks | Solid materials are separated into two flows by exploiting the different material densities.
Size separation | Materials are sorted according to their particle size. This can be carried out by drum screens, linear and circular oscillating screens, flip-flop screens, flat screens, tumbler screens and moving grates.
Vibration table | Materials are separated according to their density and size, moving (in slurry in the case of wet tables or wet density separators) across an inclined table, which oscillates backwards and forwards.
X-ray systems | Material composites are sorted according to various material densities, halogen components, or organic components, with the aid of X-rays. The characteristics of the different materials are transmitted to a data processor which controls an air jet for ejecting the materials that have been detected.
6.5. Management techniques
Accident management plan | The accident management plan is part of the EMS (see BAT 1) and iden­ tifies hazards posed by the plant and the associated risks and defines measures to address these risks. It considers the inventory of pollutants present or likely to be present which could have environmental con­ sequences if they escape.
Residues management plan | A residues management plan is part of the EMS (see BAT 1) and is a set of measures aiming to (1) minimise the generation of residues arising from the treatment of waste; (2) optimise the reuse, regeneration, re­ cycling and/or recovery of energy of the residues, and (3) ensure the proper disposal of residues.