## EA RFI for issue
Project: | InterGen Power Station Variation
Date Created: | 2025-06-05
Application Reference: | EPR/EP3833LY/V004
Operator: | Coryton Energy Company LTD
Facility: | Coryton Power Station, The Manorway, Coryton, SS17 9GN
EA Response Deadline: | 2025-06-19
EA Questions | Response
Medium Combustion Plants (MCP) at the installation.
1) Form C2.5, Combustion Plant List Spreadsheet The Eastings and Northings for the listed MCPs in the Combustion Plant List Spreadsheet (InterGen MCP-generator-list for Issue) are incorrect. Please can you check the Eastings and Northings and re-submit the spreadsheet with the correct values. | The MCP spreadsheet has been updated to reflect correct MCP coordinates. The NGR is aprovided as well as lat, long decimal co-ordinates. See screenshot to the right hand side.
Application forms
2) Form F1, Qu 2 & 5 Company Name The Company name given in Form F1 questions 2 and 5 does not match the registered company name on Companies House. The company name in the application form has to match the registered company name on Companies House. Please amend and re-submit the form. | The company name has been updated on the F1 form, from Coryton Energy Company Limited to Coryton Energy Company, Ltd.
3) Form F1, Qu 4 Confidentiality You have ticked the box in Form F1 question 4 stating that you wish us to treat specific information in your application as confidential. If this is the case, please submit a letter stating which parts of the application you deem confidential with your reasons. | The confidentiality box should not have been ticked, this was an error. The F1 form has been updated to remove this.
Environmental Risk Assessment (Air Quality Assessment)
4) Form C2, Question 6 Environmental risk assessment (Air Quality Assessment) The following aspects required by our guidance were not provided in the Air Quality Assessment: We have been unable to replicate your source terms, specifically actual H2O and O2 are not given. Additionally, all source reference conditions are given at 11% O2 and 9.6% H2O. Please can you verify that these values are correct. If they are correct, please can you provide your calculations so we can check these directly. Please see guidance at https://www.gov.uk/guidance/environmental-permitting-air-dispersion-modelling-reports#explain-emission-parameters which explains everything we require. | The g/s calculation used in theinitial assessment was incorrect (used the Actual flow not the Normalised). The base and future models have now been updated, new results produced and the report updated. Updated model input files have also been submitted.
We have identified the following habitat sites that have not been included in your air quality assessment: o Thames Estuary & Marshes (Ramsar) o Benfleet & Southend Marshes (Ramsar) o West Canvey marshes (LWS) o Northwick Farm & Seawall (LWS) o Corringham & Fobbing Marshes (LWS) | The assessment has been updated to include these sites. They have been assessed for ambient impacts, nitrogen deposition and acid deposition where applicable (based on critical loads being available on APIS (https://www.apis.ac.uk/).