## Rev Table
Site Name | Strongford STW Containment Classification Assessment
Revision | Date | Description | Author | Checked | Reviewed | Approved
1.0 | 2023-12-06 | Final Draft | M. Preisner / O.Fishwick | S. Smythe | S. Smythe | K. Chiu

## Introduction
Although this tool works as a standalone tool, we recommend you read this first: ADBA CIRIA736 Bud Classification Assessment.
There are 5 steps to follow:
1) | Identify the hazard posed to the environment by the inventory of meterials held on the site and the location of the site
a. Categorise the source
b. Identify the pathways
c. Identify the receptor
2) | The Site Hazard Rating is derived by this tool from the cobination of the hazards assessed above
3) | Calculate the likeihood of a loss of primary containment event occuring
4) | The combination of the Site Hazard Rating and the likelihood of a loss of containment occuring gives the site risk rating and requied secondary containment classification
5) | From the class of containment needed, Identify suitable designs from the 'Standard Containment Designs' Sheet
These cells are drop down menus to selected the risk category
Additional Guidance
The spreadsheets in this workbook have been created based on a protected version which did not allow for complete functionality

## 1) a) Source
| Material | Physical properties | Quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Environmental hazard rating | Justification
Process
| Digestate (fermenter) | Liquid | < 1000 | m3 | Covered Tank or lagoon |  |  |  | H | Based on latest aquatic toxicity results from REA
|  | Liquid | 1000 < X < 5000 | m3 | Covered Tank or lagoon |  |  |  | H | Based on latest aquatic toxicity results from REA
| Separated digestate solids | Cake |  |  | Concrete pad |  |  |  | M | Largely immobile therefore presents only a medium risk.
| Separated digestate liquid | Liquid |  |  | Covered tank |  |  |  | H
[8 empty] | Process Overall Rating | H | Justification: Seven digesters, two digested Sludge Storage tanks, four Blending tanks, one import well, one SAS buffer tank.
Additives and site chemicals
| Ferric Chloride | Liquid | 1 | IVC | IVC | Not flammable | No | Low | L
| Glycol | Liquid | 1 | IVC | IVC | Not flammable | No | Low | L
| Cleaning products | Liquid | 1 | IVC | Consumables container | Not flammable | No | Low | L
| Lab consumables | Liquid | 20 | litres | Consumables container | Not flammable | No | Low | L
[8 empty] | Chemicals Overall Rating | L | Section not relevant
Fire fighting agents and cooling water spillages
| Fire Fighting Agents harmful in their own right or contaminated by inventory | Liquid | >25 | m3 | NA | Not flammable | No | Low | L
| Fire fighting and cooling water contaminated by inventory | Liquid | >25 | m3 | NA | Not flammable | No | Low | L
[8 empty] | Spillages Overall Rating | L | All the hazards are "Low" therefore the overall rating is low
[8 empty] | Sources Overall Hazard Rating | H | Justification: Digesters, digested Sludge Storage tanks, Blending tanks, import well, SAS buffer tank are located at Strongford STW.
H
M
L
The table below is partially completed to show what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall source hazard rating.

## 1) b) Pathway
| Pathway - the route from primary containment to receptor |  | Environmental hazard rating | Notes
Site layout and drainage
| If any of the site inventory has a runoff time of a few minutes… |  | H | Sludge would cross the site boundary within 1 minute
| If any of the site inventory has a runoff time of a few hours.… |  | H | Not applicable
| If any of the site inventory has a runoff time of a few days… |  | M | Not applicable
| If any of the site inventory has a runoff time of a few weeks… |  | L | Not applicable
Topography, geology and hydrology
| Site is raised above a nearby receptor |  | H | Site slopes from East to West therefore is raised above the River Trent
| Chalk |  | H | According to the British Geological Survey the site is not in the chalk aquifer area.
| Fractured chalk |  | H | Not applicable
| Principal Aquifer |  | H | Aquifer of Secondary A type is present in this location
| Groundwater protection zone 1 |  | H | Groundwater Vulnerability is at Medium-Low risk according to Ground Water Vulnerability Map.
| None apply |  | L | Not relevant
Mitigation - do these apply?
| If a secondary containment system is present… |  | L | Not present at the moment
| If the rain water drainage system in the secondary containment fails safe… |  | L | Not applicable
|  | Path & Mitigation Overall Rating | H | Justification: surface water drains go to the River Trent
Climatic conditions
| Annual rainfall < 1000 mm |  | L | Annual Rainfall within 827.92 mm - 809.91 mm
| Annual rainfall > 1000 mm |  | M | Not applicable
| Snow accumulation is possible |  | M | Yes
Fire Fighting Water
| Inflammable materials normally present on site in large quantities? |  | M | Not applicable
Location
| Site is in a flood plain |  | H | Part of the site is in Flood Zone 3 and Flood Zone 2, including part of the sludge holding area on site
| Site is at bottom of a hill |  | M | The site inclines from East to West, towards the River Trent.
| Site is connected to a sewage treatment works |  | M | yes
|  | Site Considerations Overall Rating | H | Justification: Part of the site is in Flood Zone 3 and Flood Zone 2, including part of the sludge holding area on site
|  | Pathway Overall Hazard Rating | H | Justification: Site is flood Zone 2 and 3.Sludge leaves the site boundary within 1 minute.
H
M
L
The table shows what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall pathway hazard rating.

## 1) c) Receptors
| Receptors | Within | units |  | Environmental hazard rating | Notes
Watercourses and bodies
| Rivers above potable water supplies | 100 | m |  | H | River Trent is within 30m from the IED permitted Zone.
| Aquifers used for public supply | 150 | m |  | H | Aquifer of Secondary type A is present at this location.
| High quality waters | 1000 | m |  | H | Not applicable
| Agricultural abstraction points | 50 | m |  | M | No Agricultural abstraction identified via desktop analysis
| High value ecosystems | 1000 | m |  | M | Site of Special Scientific Interest and Local Nature Reserves located nearby the site
| Recreational waters | 50 | m |  | M | Not applicable
| Small treatment works | 50 | m |  | M | Not applicable
| None of the above |  |  |  | L | Not applicable
|  |  |  | Water Overall Rating | H | Justification: Site is within 100m of the River Trent
Habitation
| Dwelling | 250 | m |  | H | Housing is within 250m of the site.
| Dwelling | 251-500 | m |  | M
| Workplace | 250 | m |  | M | Middleton Livery Yard and Riding Tuition are within 250m of the site.
| None of the above |  |  |  | L | Not applicable
|  |  |  | Habitation Overall Rating | H | Justification: Housing is within 250m of the site.
Other
| SSSI/SPA/SAC | 1000 | m |  | H | King's and Hargreaves Woods SSSI 985m West.
| RAMSAR Site | 1000 | m |  | L | None identified
| None of the above |  |  |  | L | Not applicable
|  |  |  | Other Overall Rating | H | Justification: SSSI Site is within 1000m to the West.
|  |  |  | Receptors Overall Hazard Rating | H | Justification: Site is within 100m of the River Trent, with housing within 250m
H
M
L
The table shows what needs to be considered and its suggested Hazard Rating. Complete this table for your site to act as a reference and then use your judgement to assign hazard ratings in the yellow boxes. The tool then combines these to calculate the overall receptors hazard rating.
Note on K6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: According to the map it's max it is approx 30 m from the bounduary to the river

## 2) Site Hazard Rating
Calculated hazard ratings:
Source | Pathway | Receptor | Site Hazard Rating
H | H | H | High
Possible Combination |  |  | Site Hazard Rating
L | L | L | Low
M | M | L | Low
H | L | L | Low
M | M | M | Medium
H | M | L | Medium
H | H | L | Medium
H | M | M | High
H | H | M | High
H | H | H | High
Rating lookup table
L | 1
M | 2
H | 3
This assesment score
3 | 3 | 3 | 27
The table below is filled in based on your inputs in the "hazard" worksheets 1a, 1b and 1c. The tool then combines these to calculate the overall site hazard rating.
The table below shows the various combinations and their consequent overall site hazards taken from CIRIA 736 and is only provided here for your information.

## 3) Likelihood
| Risk # | Description of Risk | UNMITIGATED LIKELIHOOD | Mitigation applied | MITIGATED LIKELIHOOD |  | Low | Site Overall Likelihood
| 1 | Operational failures, such as failure of plant, or human failure by operators | H | Annual HAZOPs and operator training | L
| 2 | Shortfalls in design – lack of alarms and fail-safe devices | M | Pre-construction HAZOP identified measures - see P&IDs | L
| 3 | Structural failure – materials, components, detailing, corrosion or when exposed to heat and flame | M | Inspection of vessels, asset management | L
| 4 | Abuse – inappropriate change of use or other misuse | L |  | L
| 5 | Impact, eg from a vehicle | L | Armco barriers and concrete bollards installed | L
| 6 | Vandalism, terrorism, force majeure etc | L |  | L
| 7 | Fire or explosion | L |  | L
| 8 | Geological factors -subsidence etc | L |  | L
| 9 | Ageing or deteriorating assets/sub-components. | M | Inspection of vessels, asset management | L
| 10 | Lightning strike | L |  | L
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
| Risk | Examples of mitigation options | Reduction in likelihood | Detail of measures
| 1 | Operational Failures
|  | The team will carry out periodic design reviews and a comprehensive HAZOP involving all the designers (process, civil, drainage, electrical) to ensure primary containment failure risk is very low. In addition operator training will be strenghthened with detailed standard operating procedures. | -2 | (Taken from consultant's HAZOP report, for example)
|  | Maintenance programme in place | -1
|  | Audit process in place | -1
| 2 | Shortfalls in design
|  | Plant control will be assessed at the HAZOP stage | -2
|  | No outlets below normal liquid level | -1
| 3 | Structural failure – materials, components, detailing, corrosion or when exposed to heat and flame
|  | Pre-cast concrete tank | -2
|  | Tank design has no history of failure | -1
|  | Tank failure risk assessment completed? | -1
|  | Steel valves | -1
|  | Structures will be built to British Standards with contractors that work under ISO9000 | -1
| 4 | Abuse – inappropriate change of use or other misuse
|  | Change control procedure in place with sign off from competent personnel in applicable disciplines | -2
| 5 | Vehicle impact
|  | Armco crash barriers around tank | -2
|  | Tanks in bund not accessible by vehicles | -2
|  | Restricted vehicular access to site | -1
| 6 | Vandalism, terrorism, force majeure etc
|  | lockable valves on outlets (that are locked when not in use by procedure) | -1
|  | automatic and manual shut off valves | -1
|  | The site will include fencing where access is open to public | -1
|  | Passive CCTV system | -1
|  | Monitored CCTV with motion detection and warning signs | -2
| 7 | Fire or explosion
|  | DSEAR assesment completed | -2
|  | Control of ignition sources on site | -1
| 8 | Geological factors -subsidence etc
|  | Site investigatons will be provided to the civil contractor for the desing of the foundations | -1
| 9 | Ageing or deteriorating assets/sub-components.
|  | Ageing/deterioration factored into plant design | -1
| 10 | Lightning strike
|  | Catenary or multiple lightning conductors supplied by specialists | -1
High
Medium
Low
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
In terms of likelihood of a loss of containment, CIRIA 736 provides these guidelines on quantifying the likelihood...
To derive the likelihood for your site, firstly, using the completed risk descriptions and any additional risks identified at your site ask yourself how often will the risk occur and cause a loss of primary containment.
Secondly, consider any mitigation (see the examples provided in the table starting below row 50 for guidance) and apply the reduced likelihood.
Finally, select the likelihood by applying the fact that the highest likelihood gives the site's overall likelihood.

## 4) Site Risk and Classification
| Site Hazard Rating | Likelihood | Overall Site Risk Rating | Indicated Class of Secondary Containment Required
| High | Low | Medium | Class 2
Rating lookup table
Low | 1
Medium | 2
High | 3
This assesment score
3 | 1 |  | 3
The table below is filled in based on your inputs in the "Site Hazard Rating" worksheet and "Likelihood" worksheet. The tool then combines these to calculate the overall site hazard rating and the consequent class of secondary containment required.

## 5) Standard Containment Designs
# | Material | When used | How | Why
A | Clay | If plentiful on site | 1m thick, sheepsfoot roller etc. | Low cost & effective.
B | Stabilised soil | If soil tested and is suitable | Sample and test to determine amount of lime, cement and depth. | Low cost & effective when no clay on site.
C | Bentonite matting | If A or B not suitable | Prepare sub, roll out and cover. | Moderate cost. Quick & easy to lay. Tolerant of damage.
D | Landfill liner type foil | If A, B or C not suitable | Prepare sub, roll out, weld and cover.
E | Concrete | Small areas only | Shutter, place mesh and pour fibre reinforced. | Only if A, B, C or D not suitable.
The text and diagrams below are intended to provide an introduction to the design requirements of secondary containment systems. All this text should be read in order to gain a useful understanding of containment construction prior to commencing procurement.