## Backcalculation AA
|  |  |  | Discharge Rate (C ) | 150 | m3/day
[5 empty] | 0.0017361 | m3/s
|  |  |  | Receiving Water Flow Rate (D ) | 0.134 | m3/s
|  |  |  | Dilution Factor | 78.184
|  |  |  | Sewage Reduction Factor (E ) | 1
Substance | Discharge | Discharge | River Flow | STW | Discharge | Background | Process | Conc | EQS (AA) | Test 1 | Test 2 | Test 3 | Test 4
| Conc | Rate | Rate | Reduction | Conc | Conc | Contribution | after |  | (% of EQS) |  | PEC-BC | EQS-PEC
| (site) |  |  |  | (to River) |  |  | mixing |  |  |  | EQS
| RC-Source | EFR | RFR | STRF | RC-Process | BC | PC | PEC |  | Test Threshold 10% | Test Threshold 4% | Test Threshold 10%
Major Components | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Ammoniacal-N | 4.8 | 0.0017361 | 0.134 | 1 | 4.8 | 0.15 | 0.062189 | 0.20948 | 0.6 | 800% | 10.36% | 9.913% | 0.39052
BOD | 39 | 0.0017361 | 0.134 | 1 | 39 | 0.5 | 0.50529 | 0.99243 | 5 | 780% | 10.11% | 9.849% | 4.0076
Chloride | 1970 | 0.0017361 | 0.134 | 1 | 1970 | 29 | 25.5234 | 53.8261 | 250 | 788% | 10.21% | 9.93% | 196.1739
Sulphate | 3150 | 0.0017361 | 0.134 | 1 | 3150 | 40 | 40.8116 | 79.778 | 400 | 787.5% | 10.2% | 9.944% | 320.222
Metals | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Mercury | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No AA EQS
Cadmium | 0.0019 | 0.0017361 | 0.134 | 1 | 0.0019 | 2.5e-05 | 2.4617e-05 | 4.8982e-05 | 0.00025 | 760% | 9.847% | 9.593% | 0.00020102
Chromium | 0.037 | 0.0017361 | 0.134 | 1 | 0.037 | 0.00047 | 0.00047937 | 0.00093723 | 0.0047 | 787.2% | 10.2% | 9.941% | 0.0037628
Copper (dissolved) | 0.19 | 0.0017361 | 0.134 | 1 | 0.19 | 0.00242 | 0.0024617 | 0.0048192 | 0.0242 | 785.1% | 10.17% | 9.914% | 0.019381
Nickel (dissolved) | 0.113 | 0.0017361 | 0.134 | 1 | 0.113 | 0.00097 | 0.001464 | 0.0024029 | 0.01442 | 783.6% | 10.15% | 9.937% | 0.012017
Lead (dissolved) | 0.058 | 0.0017361 | 0.134 | 1 | 0.058 | 0.00013 | 0.00075145 | 0.00087018 | 0.00744 | 779.6% | 10.1% | 9.949% | 0.0065698
Zinc (dissolved) | 0.254 | 0.0017361 | 0.134 | 1 | 0.254 | 0.0042 | 0.0032908 | 0.007395 | 0.03219 | 789.1% | 10.22% | 9.926% | 0.024795
Pesticides / Herbicides | ug/l |  |  |  | ug/l | ug/l | #VALUE! | #VALUE! | ug/l | #VALUE! | #VALUE!
MCPP (Mecoprop) | 0.4 | 0.0017361 | 0.134 | 1 | 0.4 | 0.02 | 0.0051824 | 0.02486 | 18 | 2.222% | 0.02879% | N/A | N/A
MCPB | 0.02 | 0.0017361 | 0.134 | 1 | 0.02 | 0.02 | 0.00025912 | 0.02 | 18 | 0.1111% | 0.00144% | N/A | N/A
Dichlorprop | 0.02 | 0.0017361 | 0.134 | 1 | 0.02 | 0.02 | 0.00025912 | 0.02 | 10 | 0.2% | 0.002591% | N/A | N/A
Chlorobenzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 100 | 1% | 0.01296% | N/A | N/A
1,4 Dichlorobenzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 100 | 1% | 0.01296% | N/A | N/A
Benazolin | 0.02 | 0.0017361 | 0.134 | 1 | 0.02 | 0.02 | 0.00025912 | 0.02 | 0.5 | 4% | 0.05182% | N/A | N/A
Hydrocarbons | ug/l |  |  |  | ug/l | ug/l | #VALUE! | #VALUE! | ug/l | #VALUE! | #VALUE!
Benzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 10 | 10% | 0.1296% | N/A | N/A
Ethylbenzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 30 | 3.333% | 0.04319% | N/A | N/A
Toluene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 74 | 1.351% | 0.01751% | N/A | N/A
p-isopropyltoluene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 74 | 1.351% | 0.01751% | N/A | N/A
m,p-xylene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 30 | 3.333% | 0.04319% | N/A | N/A
o-xylene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 30 | 3.333% | 0.04319% | N/A | N/A
1,2,4-Trimethylbenzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 30 | 3.333% | 0.04319% | N/A | N/A
1,3,5-Trimethylbenzene | 1 | 0.0017361 | 0.134 | 1 | 1 | 1 | 0.012956 | 1 | 30 | 3.333% | 0.04319% | N/A | N/A
Naphthalene | 5 | 0.0017361 | 0.134 | 1 | 5 | 5 | 0.06478 | 5 | 2 | 250% | 3.239% | 0% | 2.5
Manganese (dissolved) | 2.5 | 0.0017361 | 0.134 | 1 | 2.5 | 0.032336 | 0.03239 | 0.063898 | 0.32336 | 773.1% | 10.02% | 9.761% | 0.25946
Iron | 7.8 | 0.0017361 | 0.134 | 1 | 7.8 | 0.1 | 0.10106 | 0.19849 | 1 | 780% | 10.11% | 9.849% | 0.80151
Other | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Antimony | 0.039 | 0.0017361 | 0.134 | 1 | 0.039 | 0.0005 | 0.00050529 | 0.00099243 | 0.005 | 780% | 10.11% | 9.849% | 0.0040076
Molybdenum | 0.55 | 0.0017361 | 0.134 | 1 | 0.55 | 0.007 | 0.0071258 | 0.013945 | 0.07 | 785.7% | 10.18% | 9.922% | 0.056055
Selenium | 0.078 | 0.0017361 | 0.134 | 1 | 0.078 | 0.001 | 0.0010106 | 0.0019849 | 0.01 | 780% | 10.11% | 9.849% | 0.0080151
Boron | 15.7 | 0.0017361 | 0.134 | 1 | 15.7 | 0.2 | 0.20341 | 0.39825 | 2 | 785% | 10.17% | 9.913% | 1.6017
Cyanide (free) | 0.0076 | 0.0017361 | 0.134 | 1 | 0.0076 | 0.0001 | 9.8466e-05 | 0.00019593 | 0.001 | 760% | 9.847% | 9.593% | 0.00080407
Orthophosphate | 1 | 0.0017361 | 0.134 | 1 | 1 | 0.14 | 0.012956 | 0.151 | 0.12 | 833.3% | 10.8% | 9.166% | -0.031
Organic Substances | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Benzene | 0.078 | 0.0017361 | 0.134 | 1 | 0.078 | 0.001 | 0.0010106 | 0.0019849 | 0.01 | 780% | 10.11% | 9.849% | 0.0080151
Toluene | 0.58 | 0.0017361 | 0.134 | 1 | 0.58 | 0.0074 | 0.0075145 | 0.014724 | 0.074 | 783.8% | 10.15% | 9.897% | 0.059276
Ethylbenzene | 0.58 | 0.0017361 | 0.134 | 1 | 0.58 | 0.0074 | 0.0075145 | 0.014724 | 0.074 | 783.8% | 10.15% | 9.897% | 0.059276
Xylene | 0.234 | 0.0017361 | 0.134 | 1 | 0.234 | 0.001 | 0.0030317 | 0.0039801 | 0.03 | 780% | 10.11% | 9.934% | 0.02602
Phenol | 0.06 | 0.0017361 | 0.134 | 1 | 0.06 | 0.00077 | 0.00077736 | 0.0015276 | 0.0077 | 779.2% | 10.1% | 9.839% | 0.0061724
Naphthalene | 0.015 | 0.0017361 | 0.134 | 1 | 0.015 | 0.0002 | 0.00019434 | 0.0003893 | 0.002 | 750% | 9.717% | 9.465% | 0.0016107
Mecoprop | 0.14 | 0.0017361 | 0.134 | 1 | 0.14 | 0.0018 | 0.0018138 | 0.0035676 | 0.018 | 777.8% | 10.08% | 9.82% | 0.014432
Upstream data
10% of EQS used as background due to limited or no data
Downstream data
PNEC used
Note on J16: Based on 'Good' with high alkalinity
Note on J17: Based on 'Good' with high alkalinity
Note on J22: Based on high alkalinity
Note on J57: No EQS - substituted with similar substance (toluene)

## Backcalculation MAC
|  |  |  | Discharge Rate (C ) | 150 | m3/day
[5 empty] | 0.0017361 | m3/s
|  |  |  | Receiving Water Flow Rate (D ) | 0.134 | m3/s
|  |  |  | Dilution Factor | 78.184
|  |  |  | Sewage Reduction Factor (E ) | 1
Substance | Discharge | Discharge | River Flow | STW | Discharge | Background | Process | Conc | EQS (MAC) | Test 1 | Test 2 | Test 3 | Test 4
| Conc | Rate | Rate | Reduction | Conc | Conc | Contribution | after |  | (% of EQS) |  | PEC-BC | EQS-PEC
| (site) |  |  |  | (to River) |  |  | mixing |  |  |  | EQS
| RC-Source | EFR | RFR | STRF | RC-Process | BC | PC | PEC |  | Test Threshold 10% | Test Threshold 4% | Test Threshold 10%
Major Components | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Ammoniacal-N | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
BOD | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Chloride | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Sulphate | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Metals | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Mercury | 0.00055 | 0.0017361 | 0.134 | 1 | 0.00055 | 7e-06 | 7.1258e-06 | 1.3945e-05 | 7e-05 | 785.7% | 10.18% | 9.922% | 5.6055e-05
Cadmium | 0.0115 | 0.0017361 | 0.134 | 1 | 0.0115 | 0.00015 | 0.00014899 | 0.00029517 | 0.0015 | 766.7% | 9.933% | 9.678% | 0.0012048
Chromium | 0.25 | 0.0017361 | 0.134 | 1 | 0.25 | 0.0032 | 0.003239 | 0.0063567 | 0.032 | 781.2% | 10.12% | 9.865% | 0.025643
Copper | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Nickel | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Lead | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Zinc | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Pesticides / Herbicides | n/a |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
MCPP (Mecoprop) | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
MCPB | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Dichlorprop | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Chlorobenzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
1,4 Dichlorobenzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Benazolin | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Hydrocarbons | n/a |  |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Benzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Ethylbenzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Toluene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
p-isopropyltoluene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
m,p-xylene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
o-xylene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
1,2,4-Trimethylbenzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
1,3,5-Trimethylbenzene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Naphthalene | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Manganese (dissolved) | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Iron | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Other | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Antimony | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Molybdenum | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Selenium | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Boron | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Cyanide (free) | 0.039 | 0.0017361 | 0.134 | 1 | 0.039 | 0.0005 | 0.00050529 | 0.00099243 | 0.005 | 780% | 10.11% | 9.849% | 0.0040076
Orthophosphate | n/a | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | No MAC EQS
Organic Substances | mg/l | m3/s | m3/s | Factor | mg/l | mg/l | mg/l | mg/l | mg/l
Benzene | 0.39 | 0.0017361 | 0.134 | 1 | 0.39 | 0.005 | 0.0050529 | 0.0099243 | 0.05 | 780% | 10.11% | 9.849% | 0.040076
Toluene | 3 | 0.0017361 | 0.134 | 1 | 3 | 0.038 | 0.038868 | 0.075885 | 0.38 | 789.5% | 10.23% | 9.97% | 0.30412
Ethylbenzene | 3 | 0.0017361 | 0.134 | 1 | 3 | 0.038 | 0.038868 | 0.075885 | 0.38 | 789.5% | 10.23% | 9.97% | 0.30412
Xylene | 0.235 | 0.0017361 | 0.134 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Phenol | 0.36 | 0.0017361 | 0.134 | 1 | 0.36 | 0.0046 | 0.0046642 | 0.0091457 | 0.046 | 782.6% | 10.14% | 9.882% | 0.036854
Naphthalene | 1.02 | 0.0017361 | 0.134 | 1 | 1.02 | 0.013 | 0.013215 | 0.02588 | 0.13 | 784.6% | 10.17% | 9.908% | 0.10412
Mecoprop | 1.45 | 0.0017361 | 0.134 | 1 | 1.45 | 0.0187 | 0.018786 | 0.037007 | 0.187 | 775.4% | 10.05% | 9.79% | 0.14999
Upstream data
10% of EQS used as background due to limited or no data
Downstream data
PNEC used
Note on J22: Based on high alkalinity
Note on J56: 95th Percentile
Note on J57: No EQS - substitued with similar substance (toluene)
Note on J59: 95th Percentile
Note on J61: 95th Percentile