## EA_Comments
Revision: |  | 1
Title: |  | Application Reference EPR/XP3321GD/V005 - variation of construction sewage treatment plant permit Action tracker
Reviewer(s): |  | (redacted)
Received for review on: |  | 2023-08-14
Action | Source Initials | Date | Page/ Paragraph | Reviewer's Comment | NNB Response | EA Response
High Priority
1a | EA | 2023-08-14 | n/a | This request is in regard to comments previously raised at the pre-application meeting held on 18/05/2023, and as previously detailed via comment/issue EA1 (high priority), as we raised in our pre-application review comments to you via e-mail on 26/05/2023). To enable us to determine the proposed permit variation, we need the total DIN (dissolved inorganic nitrogen) profile values in addition to the ammonia values to be provided to allow us to begin our determination of the proposed application. Therefore please provide the DIN data to us in a format that will allow us to repeat the modelling in CORMIX, so that we can check and validate the proposed plume outcomes. To date, we have only received the 20mg/l ammonia (with a 12°C temperature) CORMIX files. This information is required, as we need to understand the total DIN being discharged from the jetty from all HPC WDA permits, as we will need to complete an in-combination assessment for both our Habitats Regulations Assessment (HRA), and our Water Framework Directive (WFD) assessment. We also require the total DIN to understand the size of the plumes created. | As discussed in the pre-app meeting, we are not required to monitor for DIN within the sewage effluent discharge and therefore the data requested does not exist. it is also noted that the design guidance for sewage plants (Flows and Loads) does not include such information. The modelling in TR428 included 20mg/l of DIN from the residual ammonia in the CSTP discharge but no additional DIN was considered from this source. It was agreed at the pre-application meeting that we would provide the DIN data that does exist (i.e. for activities E2 and H of the CWDA permit), which we have done in Appendix C of the report. There was no request made at the pre-app for the CORMIX model to be updated to explicitly consider DIN in support of the CSTP variation. The CEFAS report provided in Appendix B of the application (TR428) includes a summary of the CPM modelling completed (Appendix F therein). This work was undertaken to support variation 009 and 010 of the CWDA permit including the cold commissioning effluent. This demonstrates that it is not nutrient levels that control production in the estuary and therefore the additional DIN will not adversely affect the ecological health of the estuary. Furthermore, it is noteworthy that for the bulk of the other effluents discharged via outlet 12, ammoniacal nitrogen and DIN values are identical (Groundwater and commissioning effluent) and in the case of the commissioning effluent very conservative. A small increase in allowable DIN has recently been requested to address naturally occurring nitrogenous compounds in tunnel effluent but this will not significantly change the conclusions of the modelling and assessments previously reported; the WFD status of Bridgwater Bay will not be threatened by this change.
1b | EA | 2023-08-14 | n/a | It was also stated that CPM modelling has been previously completed, and that this has shown no impact from DIN. This supporting evidence/information also has to be submitted with the permit application, and the supporting information must also be either updated to reflect the latest total DIN, or a discussion provided of the differences in the DIN between current values and modelling included. | the CPM model is described in TR428 (Appendix F therein). The model files will be transmitted formally via NNB's document manamgent system.
2a | (redacted) | 2023-08-14 | n/a | Please confirm if the flow rates presented in your supporting information are appropriate, and that these are consistent with your initial volume/flow estimates. It was mentioned during the pre-application meeting held on 18/05/2023 that discharge volumes/flows were potentially lower than anticipated, which could impact on the concentration(s) of ammonia being discharged (e.g. lower discharge volume discharge overall but containing a higher ammonia concentration). Please ensure that any CORMIX files provided to us incorporate any of the above aspects. | As detailed in Section 3.1 of the supporting report, there is no requirement for an increase in flow rates as the effluent volumes per person produced by the site are lower that the "book values" used for design. Therefore, the additional site numbers can be accommodated within the existing flow rate. The modelled flow rates therefore remain appropriate recognising that the flow rate was always a maximum and weekly and diurnal variations would always occur due as site numbers vary. The CORMIX models previously provided therefore accurately represent the peak flow rates.
2b |  | 2023-08-14 | n/a | Are bacterial processes operating as planned, and thus ammonia levels as expected? | As detailed in 2.1.1, the plant operates well when receiving consistent effluent at consistent flow rates, but the variability inherent within the operation of a biological STP on a construction site leads to challenges with the operation. As discussed in Section 2.1.2 many modifications have been made to help the plant manage this variability but there is no deployable solution that will ensure full compliance with the permit even with the current site population. Winter temperatures, especially if coincident with very low workforce numbers give rise to a significant risk to the plant.
3 | (redacted) | 2023-08-14 | n/a | To allow us to begin our determination of the variation application, we require you to provide all the CORMIX files and DIN profile information (as additionally discussed via information request 1) that support the proposed increase of the current 20mg/l limit for Ammoniacal Nitrogen to 80mg/l limit that you have applied for, along with maximum temperature data (as we will need to consider the worst possible case scenario for our assessment of your proposed variation application) However, presently we only have access to the 20mg/l CORMIX file outputs. Therefore, we require you to provide us with the 80mg/l CORMIX files and outputs, and all calculation spreadsheets used to derive the values provided in the results of your supporting information report (reference: 101121252). | The CORMIX model has not been run for a specific concentration of ammonium; rather it has been run to extract the amount of dilution provided at certain distances from the discharge point at 5 different tide states - these dilution rates are shown in Figures 8 to 12 in the TR581 report. The assessment methodology is therefore: 1. to calculate the dilution needed for the discharged concentration to decline to the EQS (Table 4) 2. Use the graphs in Figures 8 to 12 to determine the discharge from the discharge point that the plume ahs to travel to reach the EQS for each tide state 3. Present the distance (Table 5) and then discuss the significance of this for; CEFAS conclude that given the very small area of the estuary impacted there is no significant effect NBNB acknowledges that including "20mg" in the file name has contributed to the confusion on this matter but the concentration is not relevant for the model outputs. As noted in response to question 1, DIN data does not exist for the sewage discharges from site.
Medium Priority
4 | (redacted) | 2023-08-14 | 15/ Fig. 1 | Time series omits site C4, but is included within figure caption with caption stating "C1 to C8". Displaying all plots on top of one another makes it difficult to determine relative differences between sites, consider splitting out. | NNB notes that the comment made in the pre-application review was that amending the figure should be "considered" rather than being a pre-requisite for duly making the application. This figure is a duplicate of one also included in Report TR428 to which no objections were raised during previous applications. It's only purpose for including it in TR581 was to set the baseline for comparison in the later discussion. Expanded versions of "higher flow" assessment plots (Figures 18 to 25) do show C4 and given this is a worse case than that represented in Figure 1. Nothwithstanding this, for clarity NNB intends to request an an updated version of the report from CEFAS with separate plots in due course.
5 | (redacted) | 2023-08-14 | 33/Fig. 13 & 14 | Displaying all plots on top of one another makes it difficult to determine relative differences between sites, consider splitting out. | Separate plots of each of these curves are provided in Appendix A to report TR581 as stated in the paragraph above the figures.
6a | (redacted) | 2023-08-14 | 39/Fig. 15, 41/ Fig. 16, 42/ Fig. 17 | Information requests 6a and 6b are in regard to Appendix A, figures 15, 16 and 17 of TR581 v4, pages 40, 42 and 43 (pages 57, 59 and 60 of 194 of the main supporting information report PDF), as previously detailed via comment/issue 6 (medium priority). As raised in our pre-application comments to you via e-mail on 26/05/2023). 6a) The scaling of these three figures needs to be improved to allow us to accurately review and assess them (as the scaling needs to be improved to match that provided in figure 3, page 18 of TR581 v4, page 35 of the main supporting information report PDF) | NNB notes that the pre-application comment stated only that amending the scaling "could be improved" not that this was a requirement. Scaling of each figures was amended to make Figures 15, 16 and 17 consistent with each other to aid comparison. In each figure the upper box shows the jetty, with the discharge plume close to the end and the Sabellaria alveolata areas. The lower box is "zoomed in" to show the (lack of) interaction with the Corallina spp. communities. The jetty was deliberately omitted from these as, given the very limited extent of the plume, its inclusion made the figures harder to read. In the lower box the discharge point is in the centre of the darker shading.
6b |  | 2023-08-14 | 39/Fig. 15, 41/ Fig. 16, 42/ Fig. 17 | Additionally, please also amend figures 15, 16 and 17 to include the locations of features such as the jetty and Inter-tidal/sub-tidal Sabellaria (for example, as you have displayed in figure 3). Providing this information will aid our interpretation of these figures for the determination of the variation application. | The inter- and sub-tidal Sabellaria sp. are already shown in the upper box of each of these figures.
7 | (redacted) | 2023-08-14 | TR581 Page 15 | Appendix A (TR581 v4, page 15) states: “As the discharges considered in this report are released at ambient sea temperature and are not considered to be heated…”. During the pre-application meeting we had on the 18/05/2023, it was suggested that the discharge effluent could indeed be heated (as it was mentioned that the effluent would be significantly hotter than the ambient temperature of the surrounding receiving waterbody, as the effluent would be sat/contained in pipework for a significant proportion of the working day, resulting in the effluent’s temperature increasing). Please provide clarification on this point to address disparities related to temperature. As part of this clarification, please confirm: • How high does the effluent discharged temperature get? • What values have you utilised to calculate the ambient density for water receiving the discharge? • What are the potential uplift values between the discharge effluent and ambient? Are these considered throughout the year as this will impact the mixing and buoyancy of the plume? | The discharge is at ambient temperature only and as set out in the report the buoyancy applied in the modelling is based on the density difference between freshwater and saltwater as has been the case for all discharges considered for discharge via Outlet 12. The comment on the 18/05/2023 was in response to a comment from the Environment Agency around seasonal temperature variations and was to indicate that while the sea temperature may be warmer in the summer the effluent would also be warmer; there is no data on the temperature of HPC's effluent at the discharging point. Temperature was not used in the boyancy assessment. As the discharge is freshwater entering a saline water body it will always be bouyant.
8 | (redacted) | 2023-08-14 | CORMIX files | Report states 12.5 C discharge temperature, value used in CORMIX appears to be 12 C. Slight difference in value, no discernible reason given, potential impact on plume size and shape. | Footnote 1 on page 15 of TR581 (page 31 in the combined file) provides further detail regarding the slight variance the temperature used in CORMIX and the temperature used in the un-ionised ammonia calculation. Re-running the CORMIX model at 12.5° increases the distance before the EQS is reached by 3cm only.
9a | (redacted) | 2023-08-14 | CORMIX files | Lack of wind parameter in the CORMIX simulations, is this just to be conservative? This was the answer suggested in the meeting (18/05/23) however, clarity within the report on parameter selection would be useful. | Section 2.3 of CEFAS report TR581 (3rd paragraph, top of page 15 of TR581, page 32 of the combined document) provides a justification for excluding wind from the CORMIX model. CORMIX only includes wind to deal with heat loss but as in this case the discharge is at ambient temperature wind-induced heat loss is not relevant as it would apply equally to the discharge and the receiving water.
9b |  | 2023-08-14 | CORMIX files | Similarly information on why the manning value of 0.02 was selected for the modelling, to clarify reasoning. | This Manning's Number used has been used previously in all the CORMIX models for HPC and has therefore been accepted. CEFAS has provided the following response. The Manning's Number in CORMIX is a measure of the bed roughness; the cormix manual describes example ranges and gives 0.02 as a lower end value corresponding to ‘smooth earth channel, no weeds’. This value has been used as it describes a worst-case for mixing (i.e. the smoothest environment likely to be encountered) and therefore would give the most conservative (largest) estimates of the mixing range. We would further note that the CORMIX manual states ‘The friction parameters influence the mixing process only in the final far-field diffusion stage, and do not have a large impact on the predictions.’ And therefore we would not expect variance in the Manning's Number to influence the results to a significant degree.
10 |  | 2023-08-14 |  | On the 12/07/2023, we received from you via e-mail an Excel spreadsheet containing some DIN values within the spreadsheet referenced ‘20230712- HPC DIN Amm_N data’. This data is also provided in Appendix C (Ammoniacal nitrogen and DIN data for Outlet 12 effluents) of the main permit variation application supporting information report as ‘C.1 Groundwater and Tunnel Effluent data’ (pages 185 to 193 of the main report PDF) Our OCS marine water quality team are unsure what context this data has. Therefore, please provide context and clarification regarding this data, and how this data is applicable to the permit variation assessment. This clarification will allow us to more accurately review and better interpret this data. | This is the DIN data for the other discharges from the same point (i.e. under the CWDA permit) that was requested at the pre-application meeting. This is the total of the DIN data held for discharges from the site.
11a |  | 2023-08-14 |  | 11a) We therefore require you to provide details of the other protected site features for the Severn Estuary SAC, as well as the wider qualifying features of the Severn Estuary SPA and Ramsar designations, and how the features of these European designated sites have been considered in terms of source-pathway-receptor connectivity with the proposed discharge. | TR428 has been used as the basis of numerous permit applications to allow discharge into the Severn Estuary for the jetty; no queries about the sites' identified have previously been raised. However, there are no other Natura 2000 sites within the usual screening distances. notwithstanding this, the modelling clearly shows that there is no detectable plume beyond a very small area local to the jetty itself and therefore there is no S-P-R linkage to any other sites. For information the straight line distance to the nearest point of the Afon Wysg/River Usk is over 39km and the Afon Gwy/River Wye is over 58km away. Given that the overall flow is westwards there is no pathway for direct impacts on these water course. NNB intends to engage CEFAS to update the "Shadow HRA" (TR443) to reflects the cahnges requsted in this variation in due course.
11b |  | 2023-08-14 |  | 11b) To support your response to 11a, please provide supporting figures/plots of the worst case modelled discharge plume to allow the footprint of the pollutants to shown in relation to the features of these European sites (i.e. where these features are located in comparison to the modelled plume(s)). This will also allow the distance (pathway) between the discharge point (source) and other features (receptors) of the designated sites to be determined. | The figures already provided in the report show the extents of the plume - it is hyper-local and any attempt to show it at the regional scale needed to include the Afon Gwy / River Wye and Afon Wysg / River Usk would make the plume invisible.
11c |  | 2023-08-14 |  | 11c) Please confirm if you have considered if there are any other sites that should be considered from a Habitats Regulations perspective due to migratory species using the Severn estuary to reach their SAC designated river (e.g. River Wye/Afon Gwy, and/or River Usk/Afon Wysg SACs), or if the estuary is used as functionally land. | As detailed in TR428, the plume's effects are very local to the jetty an impacting only a very small area of the Severn Estuary. The report is clear that this will have no effects on the wider protected features of the SAC (including, by implication, migratory fish) and therefore cannot impact the upstream sites.
EA // 35
EA // 36
EA // 37
EA // 38
EA // 39
EA // 40
EA // 41
EA // 42
EA // 43
EA // 44
EA // 45
EA // 46
EA // 47
EA // 48
EA // 49
EA // 50
EA // 51
EA // 52
EA // 53