## Readme
Date | 2023-09-11
Associated report | TR581
Author | DH (11/09/2023)
QC | AG (12/09/2023)
Purpose | Calculations in 'ammonia calcs' tab show the details of the GETM model extrapolation with alternative ammonia and consultation water flows.
Calculations | Columns A to H calculate the additional mass of un-ionised ammonia for the baseline flows scenarios whilst columns K to R deal with the alternate flows (the two scenarios described in TR581). Column E calculates the daily mass (in kg) of total ammonia for each of the individual streams based on the flow-column B (l/s), concentration-column C (mg/l) and duration of discharge-column D (hours converted to seconds). These are summed to calculate the daily total of total ammonia (eg cell E7). The approch is to then scale the un-ionised ammonia to the change in concentrations as determined by the percent change in total ammonia mass. The calculations in the first 'box' (baseline 20 mg/L) provide the scaling point for the new scenarios which are calculated as follows: Column G calculates the proportion of the total ammonia for each stream and multiples it against the 2 µg/l baseline as shown in Figure 1 in TR581 as a proxy for the increase in un-ionised ammonia. This value is then applied to the individual baseline time series of un-ionised ammonia shown, for example in Figure 1 TR581. Column H shows the difference from the baseline scenario. As the 20 mg/l scenario is the baseline, it shows zero percentage difference. Equally, as only the sewage stream varies in concentration under the base line flow rates, only that cell (e.g. H12, H21) shows a percentage increase in concentration. Under the alternate flows, a decrease is also seen in groundwater flow due to the reduction in flow rate.

## Ammonia calcs
Baseline - 20 mg/l | [7 empty] | Alternative Flows - 20 mg/l
Source | Fow | Concentration | Duration | Mass | Unionised ammonia | Difference from baseline |  | Source | Fow | Concentration | Duration | Mass | Unionised ammonia | Difference from baseline
| (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l) |  |  | (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l)
Sewage | 13.3 | 20 | 24 | 22.9824 | 0.10457 | 0 |  | Sewage | 23.3 | 20 | 24 | 40.2624 | 0.1832 | 0.078627
Groundwater | 25 | 4.732 | 24 | 10.2211 | 0.046508 | 0 |  | Groundwater | 15 | 4.732 | 24 | 6.1327 | 0.027905 | -0.018603
Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0 |  | Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0
|  |  | Total mass | 439.5409 | 2 | 0 | 0% |  |  |  | Total mass | 452.7325 | 2.06 | 0.060024 | 2.914%
40 mg/l | [7 empty] | 40 mg/l
Source | Fow | Concentration | Duration | Mass | unionised ammonia | Difference from baseline |  | Source | Fow | Concentration | Duration | Mass | Unionised ammonia | Difference from baseline
| (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l) |  |  | (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l)
Sewage | 13.3 | 40 | 24 | 45.9648 | 0.20915 | 0.10457 |  | Sewage | 23.3 | 40 | 24 | 80.5248 | 0.3664 | 0.26183
Groundwater | 25 | 4.732 | 24 | 10.2211 | 0.046508 | 0 |  | Groundwater | 15 | 4.732 | 24 | 6.1327 | 0.027905 | -0.018603
Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0 |  | Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0
|  |  | Total mass | 462.5233 | 2.1046 | 0.10457 | 4.969% |  |  |  | Total mass | 492.9949 | 2.2432 | 0.24323 | 10.84%
60 mg/l | [7 empty] | 60 mg/l
Source | Fow | Concentration | Duration | Mass | unionised ammonia | Difference from baseline |  | Source | Fow | Concentration | Duration | Mass | Unionised ammonia | Difference from baseline
| (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l) |  |  | (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l)
Sewage | 13.3 | 60 | 24 | 68.9472 | 0.31372 | 0.20915 |  | Sewage | 23.3 | 60 | 24 | 120.7872 | 0.54961 | 0.44503
Groundwater | 25 | 4.732 | 24 | 10.2211 | 0.046508 | 0 |  | Groundwater | 15 | 4.732 | 24 | 6.1327 | 0.027905 | -0.018603
Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0 |  | Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0
|  |  | Total mass | 485.5057 | 2.2091 | 0.20915 | 9.467% |  |  |  | Total mass | 533.2573 | 2.4264 | 0.42643 | 17.57%
80 mg/l | [7 empty] | 80 mg/l
Source | Fow | Concentration | Duration | Mass | unionised ammonia | Difference from baseline |  | Source | Fow | Concentration | Duration | Mass | Unionised ammonia | Difference from baseline
| (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l) |  |  | (l/s) | (mg/l) | (hrs) | (kg/day) | (ug/l) | (ug/l)
Sewage | 13.3 | 80 | 24 | 91.9296 | 0.4183 | 0.31372 |  | Sewage | 23.3 | 80 | 24 | 161.0496 | 0.73281 | 0.62823
Groundwater | 25 | 4.732 | 24 | 10.2211 | 0.046508 | 0 |  | Groundwater | 15 | 4.732 | 24 | 6.1327 | 0.027905 | -0.018603
Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0 |  | Commisioning | 70 | 271 | 5.95 | 406.3374 | 1.8489 | 0
|  |  | Total mass | 508.4881 | 2.3137 | 0.31372 | 13.56% |  |  |  | Total mass | 573.5197 | 2.6096 | 0.60963 | 23.36%