## Cover Sheet (NNB)
NNB GENERATION COMPANY (HPC) LTD
COMPANY DOCUMENT- 101274451
Potable Water Analysis for CWDA Variation 12
© Copyright 2024 NNB Generation Company (HPC) Limited. All rights reserved.
NNB Generation Company (HPC) Limited Registered in England and Wales. Registered No. 6937084 Registered Office: 90 Whitfield Street, London, W1T 4EZ

## Summary Table
Element | Waste Conc. Max (µg/l) | EQS (µg/l)
Copper | 101.67 | 4.76
Zinc | 133.33 | 6.8
Free Cl | 1166.67 | 10

## Original
|  |  | Free chlorine | Total chlorine | Clostridium perfring | Coliform bacteria | Escherichia coli | Presumptive coliform | Presumptive E. coli | Colour (by spectrop | Enterococci | Presumptive Enteroc | Aluminium | Copper | Iron | Manganese | Zinc | Free chlorine ATS | Total chlorine ATS | Plate count 2 day @ | Plate count 3 day @ | Appearance | Colour estimated | Conductivity | Deposit | DWI Conductivity | Odour | pH | Taste | Turbidity
SU-593293 | 15/02/2023 | HPC Fire Hydrant 1 | 0.25 | 0.33 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | 0.02 | <0.01 | 0.002 | <0.01 | 0.42 | 0.9 | 0 | 0 | 1 | <5 | 148 | 1 | 134 | 1 | 7.7 |  | 0.1
SU-593294 | 15/02/2023 | HPC Fire Hydrant 2 | 0.22 | 0.33 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.001 | <0.01 | 0.71 | 0.49 | 0 | 0 | 1 | <5 | 134 | 1 | 121 | 1 | 7.7 |  | 0.07
SU-593295 | 15/02/2023 | HPC Fire Hydrant 1 | 0.26 | 0.33 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | 0.003 | <0.01 | 0.4 | 0.38 | 0 | 0 | 1 | <5 | 130 | 1 | 118 | 1 | 7.7 |  | 0.09
SU-593296 | 15/02/2023 | HPC Fire Hydrant 3 | 0.3 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | <0.01 | 0.67 | 0.47 | 0 | 0 | 1 | <5 | 130 | 1 | 118 | 1 | 7.7 |  | 0.08
SU-593297 | 15/02/2023 | HPC Fire Hydrant 6 | 0.54 | 0.57 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | 0.002 | <0.01 | 0.63 | 0.9 | 0 | 4 | 1 | <5 | 130 | 1 | 118 | 1 | 7.7 |  | 0.12
SU-593298 | 15/02/2023 | HPC Fire Hydrant 9 | 0.26 | 0.32 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.04 | 0.016 | <0.01 | 0.4 | 0.46 | 2 | 0 | 1 | <5 | 131 | 1 | 118 | 1 | 7.6 |  | 0.37
SU-593835 | 20/02/2023 | HPC K14 Demand.S | 0.24 | 0.34 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.04 | 0.002 | <0.01 | 0.26 | 0.22 | 0 | 0 | 1 | <5 | 151 | 1 | 137 | 1 | 7.9 | 1 | <0.07
SU-593836 | 20/02/2023 | HPC K14 Tidy.Cam | 0.25 | 0.34 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | <0.01 | 0.36 | 0.4 | 0 | 0 | 1 | <5 | 128 | 1 | 116 | 1 | 8 | 1 | 0.1
SU-593837 | 20/02/2023 | HPC K14 Unites.Ye | 0.25 | 0.32 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.04 | 0.003 | 0.01 | 0.34 | 0.38 | 0 | 0 | 1 | <5 | 127 | 1 | 115 | 1 | 8 | 1 | <0.07
SU-593838 | 20/02/2023 | HPC K14 Soap.Stru | 0.27 | 0.35 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.002 | <0.01 | 0.1 | 0.13 | 0 | 0 | 1 | <5 | 127 | 1 | 115 | 1 | 7.9 | 1 | <0.07
SU-594108 | 21/02/2023 | HPC K14B Pre tens |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.14 | 0.004 | <0.01 | 0.35 | 0.36 | 0 | 0 | 1 | <5 | 129 | 1 | 117 | 1 | 8 | 1 | 0.09
SU-595195 | 03/03/2023 | PM KBJV R2X |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | 0.02 | 0.002 | <0.01 | 0.43 | 0.57 | 0 | 0 | 1 | <5 | 148 | 1 | 134 | 1 | 7.8 | 1 | 0.1
SU-595196 | 03/03/2023 | KBJV 63mm Road 2 |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | 0.002 | <0.01 | 0.38 | 0.49 | 0 | 6 | 1 | <5 | 126 | 1 | 114 | 1 | 7.9 | 1 | 0.08
SU-595672 | 09/03/2023 | HPC Toilet Block 8 | 0.15 | 0.27 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | <0.001 | <0.01 | 0.33 | 0.51 | 4 | 7 | 1 | <5 | 125 | 1 | 113 | 1 | 7.5 |  | 0.1
SU-595673 | 09/03/2023 | HPC Toilet Block 8 | 0.18 | 0.23 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | <0.01 | <0.001 | <0.01 | 0.35 | 0.53 | 3 | 4 | 1 | <5 | 150 | 1 | 136 | 1 | 7.7 |  | 0.11
SU-595855 | 13/03/2023 | HPC Inside Toilet B | <0.06 | 0.11 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | <0.001 | <0.01 | 0.16 | 0.19 | 5 | 150 | 1 | <5 | 143 | 1 | 129 | 6.2 | 8 |  | 0.16
SU-597087 | 24/03/2023 | HPC FH 18 HAN | 0.33 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 0.01 | 0.05 | 0.08 | 0.028 | 0.03 | 0.37 | 0.54 | 0 | 1 | 2.1 | <5 | 123 | 2.1 | 111 | 1 | 8.1 | 0.1 | 0.59
SU-597088 | 24/03/2023 | HPC FH 37 | 0.3 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 0.01 | 0.07 | 0.1 | 0.035 | 0.03 | 0.43 | 0.46 | 0 | 0 | 2.1 | <5 | 124 | 2.1 | 112 | 1 | 7.1 | 0.1 | 1.3
SU-597089 | 24/03/2023 | HPC FH 96 | 0.2 | 0.27 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | 0.08 | 0.037 | <0.01 | 0.46 | 0.39 | 0 | 0 | 2.1 | <5 | 128 | 2.1 | 116 | 1 | 7.5 | 0.1 | 1.3
SU-597090 | 24/03/2023 | HPC FH 45 | 0.37 | 0.37 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | 0.07 | 0.05 | 0.026 | 0.04 | 0.82 | 0.4 | 0 | 2 | 2.1 | <5 | 125 | 2.1 | 113 | 1 | 7.6 | 0.1 | 0.55
SU-597091 | 24/03/2023 | HPC FH 32 | 0.32 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 |  | 0.01 | 0.04 | 0.07 | 0.032 | 0.02 | 0.19 | 0.21 | 0 | 0 | 2.1 | <5 | 124 | 2.1 | 112 | 1 | 7.6 | 0.1 | 0.63
SU-597092 | 24/03/2023 | HPC FH 11 | 0.3 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 0.02 | <0.01 | 0.07 | 0.028 | <0.01 | 0.36 | 0.46 | 0 | 2 | 2.1 | <5 | 124 | 2.1 | 112 | 1 | 7.7 | 0.1 | 0.54
SU-597286 | 27/03/2023 | HPC NOA 63mm fe | 0.35 | 0.4 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.02 | 0.01 | <0.01 | 0.3 | 0.5 | 0 | 2 | 1 | <5 | 124 | 1 | 112 | 1 | 7.8 | 1 | 0.26
SU-597287 | 27/03/2023 | HPC HAN Parent M | 0.33 | 0.38 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.02 | 0.009 | <0.01 | 0.54 | 0.61 | 0 | 0 | 1 | <5 | 123 | 1 | 111 | 1 | 7.5 | 1 | 0.33
SU-598036 | 31/03/2023 | K8B DE-MIN LINE |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | 0.02 | 0.005 | <0.01 |  | 0.52 | 0 | 36 | 1 | <5 | 131 | 1 | 118 | 1 | 7.8 | 1 | 0.16
SU-598037 | 31/03/2023 | K19 KBJV Parent M |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | 0.005 | <0.01 |  | 0.51 | 0 | 0 | 1 | <5 | 129 | 1 | 117 | 1 | 7.7 | 1 | 0.11
SU-598622 | 06/04/2023 | HPC K19B FH77 - | 0.33 | 0.4 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | <0.01 | 0.003 | <0.01 |  |  | 0 | 1 | 1 | <5 | 152 | 1 | 137 | 1 | 7.9 | 1 | <0.07
SU-598910 | 11/04/2023 | K8B DE-MIN LINE | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.07 | <0.01 | 0.03 | 0.002 | <0.01 | 0.18 | 0.24 | >300 | >300 | 1 | <5 | 142 | 1 | 128 | 1 | 8.2 | 1 | 0.79
SU-598911 | 11/04/2023 | K19 PARENT MAI | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | 0.01 | <0.01 | 0.003 | <0.01 | 0.57 | 0.53 | 0 | 6 | 1 | <5 | 127 | 1 | 115 | 1 | 8.1 | 1 | 0.13
SU-599241 | 13/04/2023 | HPC Site HOM Bal | <0.06 | 0.16 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.27 | 0.38 | 0 | 9 | 1 | <5 | 133 | 1 | 120 | 1 | 8.1 |  | 0.12
SU-599242 | 13/04/2023 | HPC Site Hydrant N | 0.33 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 0.03 | <0.01 | 0.01 | 0.006 | <0.01 | 0.27 | 0.4 | 0 | 0 | 1 | <5 | 128 | 1 | 116 | 1 | 8 |  | 0.17
SU-599243 | 13/04/2023 | HPC Site Hydrant N | 0.33 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.005 | <0.01 | 0.2 | 0.48 | 0 | 0 | 1 | <5 | 127 | 1 | 115 | 1 | 7.7 | 1 | 0.12
SU-599244 | 13/04/2023 | HPC Site Hydrant N | 0.08 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 0.01 | <0.01 | 0.02 | 0.009 | <0.01 | 0.49 | 0.59 | 0 | 32 | 1 | <5 | 124 | 1 | 112 | 1 | 7.4 | 1 | 0.21
SU-599245 | 13/04/2023 | HPC Site Hydrant N | 0.3 | 0.34 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | 0.01 | 0.01 | 0.008 | <0.01 | 0.14 | 0.29 | 0 | 0 | 1 | <5 | 127 | 1 | 115 | 1 | 7.5 | 1 | 0.28
SU-599329 | 14/04/2023 | K14B WCC Supply | 0.36 | 0.42 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.04 | <0.01 | 0.14 | 0.037 | <0.01 | 0.68 | 0.45 | 0 | 3 | 1 | <5 | 155 | 1 | 140 | 1 | 7.8 | 1 | 1
SU-599330 | 14/04/2023 | K14B WCC Welfar | 0.35 | 0.4 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | 0.01 | 0.004 | <0.01 |  |  | 0 | 0 | 1 | <5 | 128 | 1 | 116 | 1 | 7.9 | 1 | 0.17
SU-601458 | 09/05/2023 | HPC FH84 K23B | 0.13 | 0.28 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | <0.01 | 0.39 | 0.44 | 1 | 0 | 1 | <5 | 132 | 1 | 119 | 1 | 7.9 | 1 | 0.08
SU-601459 | 09/05/2023 | HPC Linxon NFM P | 0.21 | 0.26 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | <0.01 | 0.001 | <0.01 | 0.32 | 0.48 | 0 | 4 | 1 | <5 | 184 | 1 | 166 | 1 | 7.8 | 1 | 0.11
SU-601460 | 09/05/2023 | HPC Linxon NFM 2 | 0.16 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.001 | <0.01 | 0.3 | 0.23 | 1 | 2 | 1 | <5 | 137 | 1 | 124 | 1 | 7.9 | 1 | 0.21
SU-601461 | 09/05/2023 | HPC FH41 K14 | 0.22 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | <0.01 | <0.01 | <0.01 | 0.001 | <0.01 | 0.26 | 0.34 | 0 | 1 | 1 | <5 | 133 | 1 | 120 | 1 | 7.9 | 1 | <0.07
SU-601462 | 09/05/2023 | HPC FH31 HAN | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.004 | <0.01 | 0.35 | 0.33 | 2 | 0 | 1 | <5 | 133 | 1 | 120 | 1 | 7.9 | 1 | 0.13
SU-601463 | 09/05/2023 | HPC FH10 EOA | 0.26 | 0.31 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.004 | <0.01 | 0.33 | 0.28 | 1 | 5 | 1 | <5 | 133 | 1 | 120 | 1 | 7.9 | 1 | 0.13
SU-601464 | 09/05/2023 | HPC FH2 K5 Behin | 0.25 | 0.31 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | <0.01 | 0.36 | 0.65 | 0 | 0 | 1 | <5 | 133 | 1 | 120 | 1 | 7.9 | 1 | 0.17
SU-601465 | 09/05/2023 | HPC FH42 K6 | <0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | 0.01 | 0.002 | <0.01 | 1.75 | 1.26 | 0 | 0 | 1 | <5 | 133 | 1 | 120 | 1 | 7.9 | 1 | 0.12
SU-601804 | 12/05/2023 | HPC W/O Bylor Of | 0.24 | 0.33 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.01 | 0.004 | <0.01 | 0.46 | 0.31 | 0 | 0 | 1 | <5 | 145 | 1 | 131 | 1 | 8.1 | 1 | 0.1
SU-601805 | 12/05/2023 | HPC W/O Bylor Of | 0.27 | 0.41 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.004 | <0.01 | 0.44 | 0.3 | 0 | 0 | 1 | <5 | 131 | 1 | 118 | 1 | 8.1 | 1 | 0.08
| 01/06/2023 09:20 | HPC T.C.R FEED K11J |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.01 | <0.01 | <0.01 | 0.006 | <0.01 | 0.3 | 0.32 | 0 | 0 | 1 | <5 | 136 | 1 | 123 | 1 | 7.2 | 1 | 0.11
| 21/06/2023 08:15 | HPC FH11 K23B | 0.06 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | 0.04 | 0.27 | 0.003 | 0.02 | 0.45 | 0.59 | 0 | 1 | 1 | <5 | 145 | 3.1 | 131 | 1 | 8 |  | 0.48
| 21/06/2023 08:40 | HPC FH34 K11G | 0.11 | 0.18 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.05 | <0.01 | 0.02 | 0.005 | <0.01 | 0.56 | 0.82 | 0 | 2 | 1 | <5 | 146 | 1 | 132 | 1 | 8 | 1 | 0.2
| 21/06/2023 09:10 | HPC FH62 K11J | 0.11 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.03 | 0.013 | <0.01 | 0.35 | 0.25 | 0 | 0 | 1 | <5 | 156 | 1 | 141 | 1 | 8.3 | 1 | 2.4
| 21/06/2023 09:35 | HPC FH95 K4 | 0.1 | 0.18 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.04 | <0.01 | 0.04 | 0.007 | <0.01 | 0.28 | 0.42 | 0 | 0 | 1 | <5 | 160 | 1 | 145 | 1 | 8.4 | 1 | 0.31
| 21/06/2023 10:05 | HPC FH32 K11B | 0.1 | 0.17 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 0.01 | 0.02 | <0.01 | 0.003 | 0.01 | 0.35 | 0.26 | 0 | 1 | 1 | <5 | 156 | 1 | 141 | 1 | 8.4 | 1 | 0.1
| 21/06/2023 10:30 | HPC FH42 K6A | 0.14 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.04 | <0.01 | <0.01 | 0.003 | <0.01 | 0.35 | 0.31 | 0 | 1 | 1 | <5 | 157 | 1 | 142 | 1 | 8.4 | 1 | 0.21
| 23/06/2023 08:03 | K19 parent main KBJV |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.002 | <0.01 | 0.36 | 0.38 | 0 | 6 | 1 | <5 | 147 | 1 | 133 | 1 | 8.1 | 1 | 0.08
| 23/06/2023 08:31 | K8B De-Minline KBJV |  |  | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.03 | 0.003 | <0.01 |  |  | 1 | 0 | 1 | <5 | 143 | 1 | 129 | 1 | 8.1 | 1 | 0.08
| 28/06/2023 08:27 | K28 PArent Main KBJV | 0.15 | 0.18 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.2 | 0.28 | 0 | 5 | 1 | <5 | 140 | 1 | 127 | 1 | 7.9 | 1 | 0.14
| 28/06/2023 08:45 | K28 Lab Supply KBJV | 0.13 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 |  | 0.02 | <0.01 | 0.01 | 0.003 | <0.01 | 0.17 | 0.21 | 2 | 5 | 1 | <5 | 166 | 1 | 150 | 1 | 8.2 | 1 | 0.1
| 29/06/2023 06:43 | K19 Parent Mian KBJV - ///circling.gobblers.lectures | 0.27 | 0.3 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | 0.03 | <0.01 | 0.003 | 0.03 | 0.3 | 0.32 | 2 | 10 | 1 | <5 | 144 | 1 | 130 | 1 | 8.3 | 1 | 0.13
| 29/06/2023 07:05 | K8B DE-MIN LINE KBJV - ///suffer.juggled.offhand | 0.25 | 0.27 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.01 | <0.01 | 0.28 | 0.29 | 2 | 3 | 1 | <5 | 141 | 1 | 128 | 1 | 7.6 | 1 | 0.26
| 30/06/2023 09:30 | HPC/KIIW/ Hydrant 24 Parent | <0.06 | 0.09 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | <0.01 | 0.02 | 0.007 | <0.01 | 0.23 | 0.4 | 27 | >300 | 1 | <5 | 143 | 1 | 129 | 1 | 8.1 |  | 0.34
| 30/06/2023 09:40 | HPC/KIIW/ Hydrant 24 | <0.06 | 0.08 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.01 | 0.004 | <0.01 | 0.17 | 0.46 | 7 | 280 | 1 | <5 | 142 | 1 | 128 | 1 | 8.1 |  | 0.12
| 30/06/2023 10:00 | HPC/KIIW/ Hydrant 11 | 0.1 | 0.19 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.01 | 0.008 | <0.01 | 0.22 | 0.68 | 0 | 0 | 1 | <5 | 142 | 1 | 128 | 1 | 8.2 |  | 0.16
| 07/07/2023 09:00 | HPC K19A PM | 0.13 | 0.21 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.22 | 0.1 | 0 | 0 | 1 | <5 | 149 | 1 | 135 | 1 | 8.2 | 1 | 0.11
| 07/07/2023 09:10 | HPC K19A Cabin | 0.13 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.62 | 0.37 | 1 | 0 | 1 | <5 | 145 | 1 | 131 | 1 | 8.2 | 1 | 0.11
| 13/07/2023 11:00 | HPC FH11 Parent | 0.08 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 |  | 0.02 | 0.02 | <0.01 | 0.002 | 0.01 | 0.17 | 0.18 | 1 | 5 | 1 | <5 | 147 | 1 | 133 | 1 | 7.8 | 1 | 0.11
| 13/07/2023 11:10 | HPC FH11 No 1 | 0.06 | 0.13 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.004 | <0.01 | 0.3 | 0.22 | 0 | 2 | 1 | <5 | 145 | 2.1 | 131 | 1 | 8 | 8.2 | 0.16
| 13/07/2023 11:20 | HPC Lay Flat Hose 2 | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | 0.05 | 0.22 | 0.13 | 50 | >300 | 1 | <5 | 159 | 1 | 144 | 8.2 | 7.7 | 0.1 | 0.87
| 13/07/2023 11:30 | HPC Lay Flat Hose 3 | <0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | 0.04 | 0.36 | 0.17 | 52 | >300 | 1 | <5 | 175 | 1 | 158 | 8.2 | 7.7 | 0.1 | 0.42
| 13/07/2023 11:40 | HPC Lay Flat Hose 4 | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | <0.01 | <0.01 | <0.01 | 0.002 | 0.04 | 0.35 | 0.13 | 117 | >300 | 1 | <5 | 152 | 1 | 137 | 8.2 | 7.6 | 0.1 | 0.33
| 14/07/2023 08:15 | HPC U2 HDAB building Parent K8D W47B | 0.13 | 0.21 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.002 | <0.01 | 0.09 | 0.28 | 0 | 6 | 1 | <5 | 190 | 1 | 172 | 1 | 7.9 |  | 0.12
| 14/07/2023 08:20 | HPC U2 HDAB building K8D W47B | 0.11 | 0.17 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.002 | <0.01 | 0.36 | 0.47 | 0 | 3 | 1 | <5 | 151 | 1 | 137 | 1 | 8.1 |  | 0.11
| 14/07/2023 09:00 | HPC emergency shower K14b | <0.06 | 0.12 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | 0.01 | 0.33 | 0.12 | 0 | 106 | 1 | <5 | 146 | 1 | 132 | 1 | 8 |  | 0.13
| 17/07/2023 08:37 | KBJV LAB WELFARE TAP | 0.07 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.002 | <0.01 | 0.23 | 0.24 | 4 | 21 | 1 | <5 | 150 | 1 | 136 | 1 | 8.2 | 1 | 0.13
| 17/07/2023 08:10 | HPC Parent Main Connection K28/K28B | <0.06 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 |  | 0.02 | <0.01 | <0.01 | 0.001 | <0.01 | 0.12 | 0.38 | 1 | 38 | 1 | <5 | 143 | 1 | 129 | 1 | 8.3 | 1 | 0.09
| 17/07/2023 08:20 | HPC Jacobs Kitchenette K28/K28B | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.001 | <0.01 | 0.15 | 0.22 | 19 | 39 | 1 | <5 | 143 | 1 | 129 | 1 | 8.3 | 1 | 0.08
| 19/07/2023 08:30 | HPC FH 36 K28 | 0.06 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.01 | 0.009 | <0.01 | 0.29 | 0.33 | 0 | 1 | 1 | <5 | 146 | 1 | 132 | 1 | 8.1 |  | 0.11
| 19/07/2023 09:00 | HPC FH 60 K11 | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | 0.01 | 0.06 | 0.03 | <0.01 | <0.06 | 0.22 | 39 | 289 | 1 | <5 | 142 | 1 | 128 | 1 | 7.4 |  | 0.6
| 19/07/2023 09:30 | HPC FH 77 K10 | 0.14 | 0.22 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.04 | 0.015 | <0.01 | 0.25 | 0.26 | 0 | 0 | 1 | <5 | 146 | 1 | 132 | 1 | 7.6 |  | 0.29
| 19/07/2023 10:00 | HPC FH 66 K11 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.006 | <0.01 | 0.37 | 0.24 | 0 | 2 | 1 | <5 | 173 | 1 | 156 | 1 | 7.8 |  | 0.17
| 19/07/2023 10:30 | HPC FH 22 K11 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | 0.02 | 0.01 | 0.006 | 0.01 | 0.17 | 0.25 | 0 | 4 | 1 | <5 | 156 | 1 | 141 | 1 | 8 |  | 0.17
| 19/07/2023 11:00 | HPC FH 114 K19 | 0.15 | 0.22 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.03 | 0.019 | <0.01 | 0.26 | 0.23 | 4 | 0 | 1 | <5 | 147 | 1 | 133 | 1 | 8.1 |  | 0.36
| 01/08/2023 08:40 | HPC Jacobs Toilet block internal | <0.06 | <0.06 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | <0.01 | 0.02 | 0.005 | 0.01 | 0.21 | 0.27 | >300 | >300 | 1 | <5 | 150 | 1 | 136 | 1 | 7.9 |  | 0.15
| 04/08/2023 08:00 | HPC K5A Parent Main | 0.1 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 0.02 | <0.01 | 0.04 | 0.016 | <0.01 | 0.33 | 0.37 | 0 | 11 | 1 | <5 | 150 | 1 | 136 | 1 | 7.8 | 1 | 0.35
| 04/08/2023 08:15 | HPC K5A New Filling Point | 0.11 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.04 | 0.02 | <0.01 | 0.27 | 0.31 | 0 | 4 | 1 | <5 | 151 | 1 | 137 | 1 | 7.9 | 1 | 0.42
| 08/08/2023 11:00 | HPC, W45 Bylor, Toilet 9 | 0.13 | 0.2 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.002 | <0.01 | 0.19 | 0.24 | 0 | 5 | 1 | <5 | 153 | 1 | 138 | 1 | 7.7 |  | 0.09
| 08/08/2023 11:15 | HPC, W45 Parent | 0.12 | 0.21 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.06 | 0.022 | <0.01 | 0.21 | 0.24 | 1 | 46 | 1 | <5 | 144 | 1 | 130 | 1 | 7.8 |  | 0.53
| 10/08/2023 09:00 | HPC K12 Parent | 0.09 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.001 | <0.01 | 0.14 | 0.18 | 2 | 3 | 1 | <5 | 143 | 1 | 129 | 1 | 8.3 | 1 | 0.1
| 10/08/2023 09:15 | HPC K12 Billfinger | 0.14 | 0.24 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.001 | <0.01 | 0.3 | 0.26 | 1 | 0 | 1 | <5 | 143 | 1 | 129 | 1 | 8.3 | 1 | 0.09
| 21/08/2023 07:45 | HPC FH23 K12 | <0.06 | 0.14 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.007 | <0.01 | 0.39 | 0.16 | 0 | 0 | 1 | <5 | 162 | 1 | 147 | 1 | 7.8 | 0.1 | 0.24
| 21/08/2023 08:15 | HPC FH18 K11J | 0.11 | 0.13 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.29 | 0.11 | 1 | 0 | 1 | <5 | 170 | 1 | 154 | 1 | 8.4 | 1 | 0.14
| 21/08/2023 09:00 | HPC FH2 K5C | 0.08 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | 0.03 | 0.02 | 0.007 | 0.02 | 0.45 | 0.29 | 0 | 8 | 1 | <5 | 145 | 1 | 131 | 1 | 7.9 | 1 | 0.22
| 21/08/2023 09:45 | HPC FH3 K11B | 0.06 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.01 | <0.01 | 0.21 | 0.14 | 0 | 0 | 1 | <5 | 143 | 1 | 129 | 1 | 7.9 | 1 | 0.28
| 21/08/2023 10:45 | HPC FH85 K18A | 0.06 | 0.15 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | 0.19 | 0.1 | 0.016 | 0.09 | 0.32 | 0.28 | 0 | 71 | 2.1 | >5 | 145 | 2.1 | 131 | 1 | 8 | 0.1 | 1.2
| 21/08/2023 08:30 | HPC FH 97 K4 | 0.12 | 0.25 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | 0.02 | 0.006 | <0.01 | 0.12 | 0.27 | 2 | 0 | 1 | <5 | 144 | 1 | 130 | 1 | 8 | 1 | 0.19
| 22/08/2023 09:05 | Decisions Workroom SPEEDS Parent main | 0.08 | 0.16 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.37 | 0.4 | 0 | 0 | 1 | <5 | 158 | 1 | 143 | 1 | 7.9 | 1 | 0.15
| 22/08/2023 09:20 | HArdback. Landlady. Large 25mm Service | 0.11 | 0.23 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.02 | <0.01 | <0.01 | 0.003 | <0.01 | 0.24 | 0.26 | 0 | 153 | 1 | <5 | 151 | 1 | 137 | 1 | 7.6 | 1 | 0.12
| 25/08/2023 09:00 | K15B Bylor North Toilet | 0.13 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0.7 | 5 | 5 | 0.02 | <0.01 | <0.01 | 0.002 | <0.01 |  |  | 9 | 7 | 1 | <5 | 148 | 1 | 134 | 1 | 8.2 | 1 | 0.12
| 29/08/2023 16:00 | HPC W15B HS2 Parent - Jabs, Drill, Flickers | <0.06 | 0.09 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | <0.01 | 0.03 | 0.003 | <0.01 | <0.06 | 0.36 | 106 | 154 | 1 | <5 | 152 | 1 | 137 | 6.1 | 7.5 | 1 | 0.17
| 29/08/2023 16:20 | HPC W15B HS2 Toilet Block - Skater, Crossword, Clay | <0.06 | 0.07 | 0 | 0 | 0 | 0 | 0 | <0.6 | 0 |  | 0.03 | <0.01 | 0.02 | 0.002 | <0.01 | 0.18 | 0.26 | 1 | 9 | 1 | <5 | 148 | 1 | 134 | 6.1 | 7.6 | 1 | 0.16
| 30/08/2023 08:30 | HPC W15B HS2 Jabs, drill, flickers - Parent |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0.07 | 0.19 | 0 | 0
| 30/08/2023 09:00 | HPC W15B HS2 toilet - skate crossword, clay |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0.14 | 0.23 | 2 | 3
| 30/08/2023 09:15 | HPC W15B 3 Story - hardback landlady large - parent |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0.18 | 0.39 | 0 | 0
| 30/08/2023 09:45 | HPC W13 heat sink lift - suiting gear slightly |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0.19 | 0.21 | 1 | 0
| 2023-08-30 10:15 | HPC W11 Outfall lift balfor beatty - regress outreach vote |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | [6 empty] | 0.23 | 0.49 | 0 | 0
[23 empty] | Avg. | 142.6061
[23 empty] | 95th | 166.4
[23 empty] | Waste Avg | 470.6
[23 empty] | Waste 95th | 549.12
351.4368

## < removed
| Date | Sampling site | Free chlorine | Total chlorine | Aluminium | Copper | Iron | Manganese | Zinc | Free chlorine ATS | Total chlorine ATS | Plate count 2 day @ | Plate count 3 day @ | Conductivity | Deposit | DWI Conductivity | pH | Turbidity
|  |  | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l
SU-593293 | 15/02/2023 | HPC Fire Hydrant 1 | 0.25 | 0.33 | 0.01 | 0.02 | 0.01 | 0.002 | 0.01 | 0.42 | 0.9 | 0 | 0 | 148 | 1 | 134 | 7.7 | 0.1
SU-593294 | 15/02/2023 | HPC Fire Hydrant 2 | 0.22 | 0.33 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.71 | 0.49 | 0 | 0 | 134 | 1 | 121 | 7.7 | 0.07
SU-593295 | 15/02/2023 | HPC Fire Hydrant 1 | 0.26 | 0.33 | 0.01 | 0.01 | 0.01 | 0.003 | 0.01 | 0.4 | 0.38 | 0 | 0 | 130 | 1 | 118 | 7.7 | 0.09
SU-593296 | 15/02/2023 | HPC Fire Hydrant 3 | 0.3 | 0.38 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.67 | 0.47 | 0 | 0 | 130 | 1 | 118 | 7.7 | 0.08
SU-593297 | 15/02/2023 | HPC Fire Hydrant 6 | 0.54 | 0.57 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.63 | 0.9 | 0 | 4 | 130 | 1 | 118 | 7.7 | 0.12
SU-593298 | 15/02/2023 | HPC Fire Hydrant 9 | 0.26 | 0.32 | 0.01 | 0.01 | 0.04 | 0.016 | 0.01 | 0.4 | 0.46 | 2 | 0 | 131 | 1 | 118 | 7.6 | 0.37
SU-593835 | 20/02/2023 | HPC K14 Demand.S | 0.24 | 0.34 | 0.02 | 0.01 | 0.04 | 0.002 | 0.01 | 0.26 | 0.22 | 0 | 0 | 151 | 1 | 137 | 7.9 | 0.07
SU-593836 | 20/02/2023 | HPC K14 Tidy.Cam | 0.25 | 0.34 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.36 | 0.4 | 0 | 0 | 128 | 1 | 116 | 8 | 0.1
SU-593837 | 20/02/2023 | HPC K14 Unites.Ye | 0.25 | 0.32 | 0.02 | 0.01 | 0.04 | 0.003 | 0.01 | 0.34 | 0.38 | 0 | 0 | 127 | 1 | 115 | 8 | 0.07
SU-593838 | 20/02/2023 | HPC K14 Soap.Stru | 0.27 | 0.35 | 0.02 | 0.01 | 0.02 | 0.002 | 0.01 | 0.1 | 0.13 | 0 | 0 | 127 | 1 | 115 | 7.9 | 0.07
SU-594108 | 21/02/2023 | HPC K14B Pre tens |  |  | 0.02 | 0.01 | 0.14 | 0.004 | 0.01 | 0.35 | 0.36 | 0 | 0 | 129 | 1 | 117 | 8 | 0.09
SU-595195 | 03/03/2023 | PM KBJV R2X |  |  | 0.01 | 0.01 | 0.02 | 0.002 | 0.01 | 0.43 | 0.57 | 0 | 0 | 148 | 1 | 134 | 7.8 | 0.1
SU-595196 | 03/03/2023 | KBJV 63mm Road 2 |  |  | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.38 | 0.49 | 0 | 6 | 126 | 1 | 114 | 7.9 | 0.08
SU-595672 | 09/03/2023 | HPC Toilet Block 8 | 0.15 | 0.27 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.33 | 0.51 | 4 | 7 | 125 | 1 | 113 | 7.5 | 0.1
SU-595673 | 09/03/2023 | HPC Toilet Block 8 | 0.18 | 0.23 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.35 | 0.53 | 3 | 4 | 150 | 1 | 136 | 7.7 | 0.11
SU-595855 | 13/03/2023 | HPC Inside Toilet B | 0.06 | 0.11 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.16 | 0.19 | 5 | 150 | 143 | 1 | 129 | 8 | 0.16
SU-597087 | 24/03/2023 | HPC FH 18 HAN | 0.33 | 0.48 | 0.01 | 0.05 | 0.08 | 0.028 | 0.03 | 0.37 | 0.54 | 0 | 1 | 123 | 2.1 | 111 | 8.1 | 0.59
SU-597088 | 24/03/2023 | HPC FH 37 | 0.3 | 0.38 | 0.01 | 0.07 | 0.1 | 0.035 | 0.03 | 0.43 | 0.46 | 0 | 0 | 124 | 2.1 | 112 | 7.1 | 1.3
SU-597089 | 24/03/2023 | HPC FH 96 | 0.2 | 0.27 | 0.01 | 0.01 | 0.08 | 0.037 | 0.01 | 0.46 | 0.39 | 0 | 0 | 128 | 2.1 | 116 | 7.5 | 1.3
SU-597090 | 24/03/2023 | HPC FH 45 | 0.37 | 0.37 | 0.01 | 0.07 | 0.05 | 0.026 | 0.04 | 0.82 | 0.4 | 0 | 2 | 125 | 2.1 | 113 | 7.6 | 0.55
SU-597091 | 24/03/2023 | HPC FH 32 | 0.32 | 0.33 | 0.01 | 0.04 | 0.07 | 0.032 | 0.02 | 0.19 | 0.21 | 0 | 0 | 124 | 2.1 | 112 | 7.6 | 0.63
SU-597092 | 24/03/2023 | HPC FH 11 | 0.3 | 0.37 | 0.02 | 0.01 | 0.07 | 0.028 | 0.01 | 0.36 | 0.46 | 0 | 2 | 124 | 2.1 | 112 | 7.7 | 0.54
SU-597286 | 27/03/2023 | HPC NOA 63mm fe | 0.35 | 0.4 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.3 | 0.5 | 0 | 2 | 124 | 1 | 112 | 7.8 | 0.26
SU-597287 | 27/03/2023 | HPC HAN Parent M | 0.33 | 0.38 | 0.01 | 0.01 | 0.02 | 0.009 | 0.01 | 0.54 | 0.61 | 0 | 0 | 123 | 1 | 111 | 7.5 | 0.33
SU-598036 | 31/03/2023 | K8B DE-MIN LINE |  |  | 0.01 | 0.01 | 0.02 | 0.005 | 0.01 |  | 0.52 | 0 | 36 | 131 | 1 | 118 | 7.8 | 0.16
SU-598037 | 31/03/2023 | K19 KBJV Parent M |  |  | 0.01 | 0.01 | 0.01 | 0.005 | 0.01 |  | 0.51 | 0 | 0 | 129 | 1 | 117 | 7.7 | 0.11
SU-598622 | 06/04/2023 | HPC K19B FH77 - | 0.33 | 0.4 | 0.01 | 0.01 | 0.01 | 0.003 | 0.01 |  |  | 0 | 1 | 152 | 1 | 137 | 7.9 | 0.07
SU-598910 | 11/04/2023 | K8B DE-MIN LINE | 0.06 | 0.06 | 0.07 | 0.01 | 0.03 | 0.002 | 0.01 | 0.18 | 0.24 | >300 | >300 | 142 | 1 | 128 | 8.2 | 0.79
SU-598911 | 11/04/2023 | K19 PARENT MAI | 0.35 | 0.37 | 0.01 | 0.01 | 0.01 | 0.003 | 0.01 | 0.57 | 0.53 | 0 | 6 | 127 | 1 | 115 | 8.1 | 0.13
SU-599241 | 13/04/2023 | HPC Site HOM Bal | 0.06 | 0.16 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.27 | 0.38 | 0 | 9 | 133 | 1 | 120 | 8.1 | 0.12
SU-599242 | 13/04/2023 | HPC Site Hydrant N | 0.33 | 0.37 | 0.03 | 0.01 | 0.01 | 0.006 | 0.01 | 0.27 | 0.4 | 0 | 0 | 128 | 1 | 116 | 8 | 0.17
SU-599243 | 13/04/2023 | HPC Site Hydrant N | 0.33 | 0.37 | 0.01 | 0.01 | 0.01 | 0.005 | 0.01 | 0.2 | 0.48 | 0 | 0 | 127 | 1 | 115 | 7.7 | 0.12
SU-599244 | 13/04/2023 | HPC Site Hydrant N | 0.08 | 0.14 | 0.01 | 0.01 | 0.02 | 0.009 | 0.01 | 0.49 | 0.59 | 0 | 32 | 124 | 1 | 112 | 7.4 | 0.21
SU-599245 | 13/04/2023 | HPC Site Hydrant N | 0.3 | 0.34 | 0.01 | 0.01 | 0.01 | 0.008 | 0.01 | 0.14 | 0.29 | 0 | 0 | 127 | 1 | 115 | 7.5 | 0.28
SU-599329 | 14/04/2023 | K14B WCC Supply | 0.36 | 0.42 | 0.04 | 0.01 | 0.14 | 0.037 | 0.01 | 0.68 | 0.45 | 0 | 3 | 155 | 1 | 140 | 7.8 | 1
SU-599330 | 14/04/2023 | K14B WCC Welfar | 0.35 | 0.4 | 0.01 | 0.01 | 0.01 | 0.004 | 0.01 |  |  | 0 | 0 | 128 | 1 | 116 | 7.9 | 0.17
SU-601458 | 09/05/2023 | HPC FH84 K23B | 0.13 | 0.28 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.39 | 0.44 | 1 | 0 | 132 | 1 | 119 | 7.9 | 0.08
SU-601459 | 09/05/2023 | HPC Linxon NFM P | 0.21 | 0.26 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.32 | 0.48 | 0 | 4 | 184 | 1 | 166 | 7.8 | 0.11
SU-601460 | 09/05/2023 | HPC Linxon NFM 2 | 0.16 | 0.2 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.3 | 0.23 | 1 | 2 | 137 | 1 | 124 | 7.9 | 0.21
SU-601461 | 09/05/2023 | HPC FH41 K14 | 0.22 | 0.25 | 0.01 | 0.01 | 0.01 | 0.001 | 0.01 | 0.26 | 0.34 | 0 | 1 | 133 | 1 | 120 | 7.9 | 0.07
SU-601462 | 09/05/2023 | HPC FH31 HAN | 0.06 | 0.06 | 0.01 | 0.01 | 0.01 | 0.004 | 0.01 | 0.35 | 0.33 | 2 | 0 | 133 | 1 | 120 | 7.9 | 0.13
SU-601463 | 09/05/2023 | HPC FH10 EOA | 0.26 | 0.31 | 0.01 | 0.01 | 0.01 | 0.004 | 0.01 | 0.33 | 0.28 | 1 | 5 | 133 | 1 | 120 | 7.9 | 0.13
SU-601464 | 09/05/2023 | HPC FH2 K5 Behin | 0.25 | 0.31 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 0.36 | 0.65 | 0 | 0 | 133 | 1 | 120 | 7.9 | 0.17
SU-601465 | 09/05/2023 | HPC FH42 K6 | 0.06 | 0.06 | 0.01 | 0.01 | 0.01 | 0.002 | 0.01 | 1.75 | 1.26 | 0 | 0 | 133 | 1 | 120 | 7.9 | 0.12
SU-601804 | 12/05/2023 | HPC W/O Bylor Of | 0.24 | 0.33 | 0.02 | 0.01 | 0.01 | 0.004 | 0.01 | 0.46 | 0.31 | 0 | 0 | 145 | 1 | 131 | 8.1 | 0.1
SU-601805 | 12/05/2023 | HPC W/O Bylor Of | 0.27 | 0.41 | 0.02 | 0.01 | 0.01 | 0.004 | 0.01 | 0.44 | 0.3 | 0 | 0 | 131 | 1 | 118 | 8.1 | 0.08
| 2023-05-17 10:23 | KBJV K28 LAB CANTEEN | 0.06 | 0.06 | 0.06 | 0.01 | 0.01 | 0.001 | 0.04 | 0.12 | 0.16 | >300 | >300 | 429 | 1 | 388 | 8.4 | 0.24
| 2023-05-17 10:45 | KBJV K28 LAB SINK | 0.06 | 0.06 | 0.03 | 0.01 | 0.02 | 0.001 | 0.09 | 0.13 | 0.18 | >300 | >300 | 420 | 1 | 380 | 8.5 | 0.3
| 2023-05-17 11:01 | KBJV K28 OUTSIDE SUPPLY | 0.06 | 0.06 | 0.02 | 0.01 | 0.01 | 0.001 | 0.12 | 0.14 | 0.18 | >300 | >300 | 418 | 1 | 378 | 8.5 | 0.42
| 2023-05-18 09:30 | HPC SITE F3.1 CANTEEN | 0.25 | 0.29 | 0.03 | 0.01 | 0.01 | 0.004 | 0.02 | 0.27 | 0.3 | 0 | 17 | 133 | 1 | 120 | 7.5 | 0.25
| 2023-05-18 11:00 | HPC WCC WELFARE CABIN | 0.31 | 0.33 | 0.03 | 0.01 | 0.01 | 0.005 | 0.01 | 0.32 | 0.41 | 0 | 1 | 135 | 1 | 122 | 7.8 | 0.13
| 2023-05-23 10:30 | HPC Bottle station 6 K118 | 0.27 | 0.3 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.26 | 0.27 | 0 | 1 | 148 | 1 | 134 | 8 | 0.08
| 2023-05-23 09:00 | HPC T.C.R Feed K11J | 0.23 | 0.24 | 0.21 | 0.01 | 0.02 | 0.003 | 0.01 | 0.32 | 0.36 | 0 | 1 | 145 | 1 | 131 | 8 | 0.08
| 2023-05-23 09:15 | HPC T.C.R Parent K11J | 0.23 | 0.31 | 0.02 | 0.01 | 0.06 | 0.003 | 0.01 | 0.3 | 0.35 | 0 | 0 | 140 | 1 | 127 | 8 | 0.08
| 2023-05-25 08:45 | HPC Toilet block 2/k10 Parent | 0.19 | 0.27 | 0.01 | 0.01 | 0.01 | 0.005 | 0.01 | 0.35 | 0.61 | 3 | 0 | 140 | 1 | 127 | 8 | 0.1
| 2023-05-25 08:50 | HPC Toilet block 2/k10 Feed | 0.19 | 0.25 | 0.01 | 0.01 | 0.01 | 0.004 | 0.01 | 0.19 | 0.26 | 13 | 11 | 151 | 1 | 137 | 7.9 | 0.08
| 2023-05-25 08:55 | HPC Toilet block 2/k10 inside block | 0.19 | 0.26 | 0.02 | 0.01 | 0.01 | 0.004 | 0.01 | 0.11 | 0.13 | 4 | 21 | 165 | 1 | 149 | 7.9 | 0.12
| 28/06/2023 08:45 | K28 Lab Supply KBJV | 0.13 | 0.2 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.17 | 0.21 | 2 | 5 | 166 | 1 | 150 | 8.2 | 0.1
| 29/06/2023 06:43 | K19 Parent Mian KBJV - ///circling.gobblers.lectures | 0.27 | 0.3 | 0.02 | 0.03 | 0.01 | 0.003 | 0.03 | 0.3 | 0.32 | 2 | 10 | 144 | 1 | 130 | 8.3 | 0.13
| 29/06/2023 07:05 | K8B DE-MIN LINE KBJV - ///suffer.juggled.offhand | 0.25 | 0.27 | 0.02 | 0.01 | 0.02 | 0.01 | 0.01 | 0.28 | 0.29 | 2 | 3 | 141 | 1 | 128 | 7.6 | 0.26
| 30/06/2023 09:30 | HPC/KIIW/ Hydrant 24 Parent | 0.06 | 0.09 | 0.03 | 0.01 | 0.02 | 0.007 | 0.01 | 0.23 | 0.4 | 27 | >300 | 143 | 1 | 129 | 8.1 | 0.34
| 30/06/2023 09:40 | HPC/KIIW/ Hydrant 24 | 0.06 | 0.08 | 0.02 | 0.01 | 0.01 | 0.004 | 0.01 | 0.17 | 0.46 | 7 | 280 | 142 | 1 | 128 | 8.1 | 0.12
| 30/06/2023 10:00 | HPC/KIIW/ Hydrant 11 | 0.1 | 0.19 | 0.02 | 0.01 | 0.01 | 0.008 | 0.01 | 0.22 | 0.68 | 0 | 0 | 142 | 1 | 128 | 8.2 | 0.16
| 07/07/2023 09:00 | HPC K19A PM | 0.13 | 0.21 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.22 | 0.1 | 0 | 0 | 149 | 1 | 135 | 8.2 | 0.11
| 07/07/2023 09:10 | HPC K19A Cabin | 0.13 | 0.2 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.62 | 0.37 | 1 | 0 | 145 | 1 | 131 | 8.2 | 0.11
| 13/07/2023 11:00 | HPC FH11 Parent | 0.08 | 0.2 | 0.02 | 0.02 | 0.01 | 0.002 | 0.01 | 0.17 | 0.18 | 1 | 5 | 147 | 1 | 133 | 7.8 | 0.11
| 13/07/2023 11:10 | HPC FH11 No 1 | 0.06 | 0.13 | 0.02 | 0.01 | 0.01 | 0.004 | 0.01 | 0.3 | 0.22 | 0 | 2 | 145 | 2.1 | 131 | 8 | 0.16
| 13/07/2023 11:20 | HPC Lay Flat Hose 2 | 0.06 | 0.06 | 0.01 | 0.01 | 0.01 | 0.002 | 0.05 | 0.22 | 0.13 | 50 | >300 | 159 | 1 | 144 | 7.7 | 0.87
| 13/07/2023 11:30 | HPC Lay Flat Hose 3 | 0.06 | 0.06 | 0.01 | 0.01 | 0.01 | 0.002 | 0.04 | 0.36 | 0.17 | 52 | >300 | 175 | 1 | 158 | 7.7 | 0.42
| 13/07/2023 11:40 | HPC Lay Flat Hose 4 | 0.06 | 0.06 | 0.01 | 0.01 | 0.01 | 0.002 | 0.04 | 0.35 | 0.13 | 117 | >300 | 152 | 1 | 137 | 7.6 | 0.33
| 14/07/2023 08:15 | HPC U2 HDAB building Parent K8D W47B | 0.13 | 0.21 | 0.02 | 0.01 | 0.01 | 0.002 | 0.01 | 0.09 | 0.28 | 0 | 6 | 190 | 1 | 172 | 7.9 | 0.12
| 14/07/2023 08:20 | HPC U2 HDAB building K8D W47B | 0.11 | 0.17 | 0.02 | 0.01 | 0.01 | 0.002 | 0.01 | 0.36 | 0.47 | 0 | 3 | 151 | 1 | 137 | 8.1 | 0.11
| 14/07/2023 09:00 | HPC emergency shower K14b | 0.06 | 0.12 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.33 | 0.12 | 0 | 106 | 146 | 1 | 132 | 8 | 0.13
| 17/07/2023 08:37 | KBJV LAB WELFARE TAP | 0.07 | 0.15 | 0.02 | 0.01 | 0.01 | 0.002 | 0.01 | 0.23 | 0.24 | 4 | 21 | 150 | 1 | 136 | 8.2 | 0.13
| 17/07/2023 08:10 | HPC Parent Main Connection K28/K28B | 0.06 | 0.09 | 0.02 | 0.01 | 0.01 | 0.001 | 0.01 | 0.12 | 0.38 | 1 | 38 | 143 | 1 | 129 | 8.3 | 0.09
| 17/07/2023 08:20 | HPC Jacobs Kitchenette K28/K28B | 0.06 | 0.06 | 0.02 | 0.01 | 0.01 | 0.001 | 0.01 | 0.15 | 0.22 | 19 | 39 | 143 | 1 | 129 | 8.3 | 0.08
| 19/07/2023 08:30 | HPC FH 36 K28 | 0.06 | 0.15 | 0.02 | 0.01 | 0.01 | 0.009 | 0.01 | 0.29 | 0.33 | 0 | 1 | 146 | 1 | 132 | 8.1 | 0.11
| 19/07/2023 09:00 | HPC FH 60 K11 | 0.06 | 0.06 | 0.03 | 0.01 | 0.06 | 0.03 | 0.01 | 0.06 | 0.22 | 39 | 289 | 142 | 1 | 128 | 7.4 | 0.6
| 19/07/2023 09:30 | HPC FH 77 K10 | 0.14 | 0.22 | 0.02 | 0.01 | 0.04 | 0.015 | 0.01 | 0.25 | 0.26 | 0 | 0 | 146 | 1 | 132 | 7.6 | 0.29
| 19/07/2023 10:00 | HPC FH 66 K11 | 0.1 | 0.2 | 0.02 | 0.01 | 0.01 | 0.006 | 0.01 | 0.37 | 0.24 | 0 | 2 | 173 | 1 | 156 | 7.8 | 0.17
| 19/07/2023 10:30 | HPC FH 22 K11 | 0.1 | 0.2 | 0.02 | 0.02 | 0.01 | 0.006 | 0.01 | 0.17 | 0.25 | 0 | 4 | 156 | 1 | 141 | 8 | 0.17
| 19/07/2023 11:00 | HPC FH 114 K19 | 0.15 | 0.22 | 0.02 | 0.01 | 0.03 | 0.019 | 0.01 | 0.26 | 0.23 | 4 | 0 | 147 | 1 | 133 | 8.1 | 0.36
| 01/08/2023 08:40 | HPC Jacobs Toilet block internal | 0.06 | 0.06 | 0.03 | 0.01 | 0.02 | 0.005 | 0.01 | 0.21 | 0.27 | >300 | >300 | 150 | 1 | 136 | 7.9 | 0.15
| 04/08/2023 08:00 | HPC K5A Parent Main | 0.1 | 0.16 | 0.02 | 0.01 | 0.04 | 0.016 | 0.01 | 0.33 | 0.37 | 0 | 11 | 150 | 1 | 136 | 7.8 | 0.35
| 04/08/2023 08:15 | HPC K5A New Filling Point | 0.11 | 0.2 | 0.02 | 0.01 | 0.04 | 0.02 | 0.01 | 0.27 | 0.31 | 0 | 4 | 151 | 1 | 137 | 7.9 | 0.42
| 08/08/2023 11:00 | HPC, W45 Bylor, Toilet 9 | 0.13 | 0.2 | 0.02 | 0.01 | 0.02 | 0.002 | 0.01 | 0.19 | 0.24 | 0 | 5 | 153 | 1 | 138 | 7.7 | 0.09
| 08/08/2023 11:15 | HPC, W45 Parent | 0.12 | 0.21 | 0.02 | 0.01 | 0.06 | 0.022 | 0.01 | 0.21 | 0.24 | 1 | 46 | 144 | 1 | 130 | 7.8 | 0.53
| 10/08/2023 09:00 | HPC K12 Parent | 0.09 | 0.15 | 0.02 | 0.01 | 0.01 | 0.001 | 0.01 | 0.14 | 0.18 | 2 | 3 | 143 | 1 | 129 | 8.3 | 0.1
| 10/08/2023 09:15 | HPC K12 Billfinger | 0.14 | 0.24 | 0.02 | 0.01 | 0.01 | 0.001 | 0.01 | 0.3 | 0.26 | 1 | 0 | 143 | 1 | 129 | 8.3 | 0.09
| 21/08/2023 07:45 | HPC FH23 K12 | 0.06 | 0.14 | 0.02 | 0.01 | 0.02 | 0.007 | 0.01 | 0.39 | 0.16 | 0 | 0 | 162 | 1 | 147 | 7.8 | 0.24
| 21/08/2023 08:15 | HPC FH18 K11J | 0.11 | 0.13 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.29 | 0.11 | 1 | 0 | 170 | 1 | 154 | 8.4 | 0.14
| 21/08/2023 09:00 | HPC FH2 K5C | 0.08 | 0.15 | 0.02 | 0.03 | 0.02 | 0.007 | 0.02 | 0.45 | 0.29 | 0 | 8 | 145 | 1 | 131 | 7.9 | 0.22
| 21/08/2023 09:45 | HPC FH3 K11B | 0.06 | 0.15 | 0.02 | 0.01 | 0.02 | 0.01 | 0.01 | 0.21 | 0.14 | 0 | 0 | 143 | 1 | 129 | 7.9 | 0.28
| 21/08/2023 10:45 | HPC FH85 K18A | 0.06 | 0.15 | 0.03 | 0.19 | 0.1 | 0.016 | 0.09 | 0.32 | 0.28 | 0 | 71 | 145 | 2.1 | 131 | 8 | 1.2
| 21/08/2023 08:30 | HPC FH 97 K4 | 0.12 | 0.25 | 0.02 | 0.01 | 0.02 | 0.006 | 0.01 | 0.12 | 0.27 | 2 | 0 | 144 | 1 | 130 | 8 | 0.19
| 22/08/2023 09:05 | Decisions Workroom SPEEDS Parent main | 0.08 | 0.16 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.37 | 0.4 | 0 | 0 | 158 | 1 | 143 | 7.9 | 0.15
| 22/08/2023 09:20 | HArdback. Landlady. Large 25mm Service | 0.11 | 0.23 | 0.02 | 0.01 | 0.01 | 0.003 | 0.01 | 0.24 | 0.26 | 0 | 153 | 151 | 1 | 137 | 7.6 | 0.12
| 25/08/2023 09:00 | K15B Bylor North Toilet | 0.13 | 0.19 | 0.02 | 0.01 | 0.01 | 0.002 | 0.01 |  |  | 9 | 7 | 148 | 1 | 134 | 8.2 | 0.12
| 29/08/2023 16:00 | HPC W15B HS2 Parent - Jabs, Drill, Flickers | 0.06 | 0.09 | 0.03 | 0.01 | 0.03 | 0.003 | 0.01 | 0.06 | 0.36 | 106 | 154 | 152 | 1 | 137 | 7.5 | 0.17
| 29/08/2023 16:20 | HPC W15B HS2 Toilet Block - Skater, Crossword, Clay | 0.06 | 0.07 | 0.03 | 0.01 | 0.02 | 0.002 | 0.01 | 0.18 | 0.26 | 1 | 9 | 148 | 1 | 134 | 7.6 | 0.16
| 30/08/2023 08:30 | HPC W15B HS2 Jabs, drill, flickers - Parent | [7 empty] | 0.07 | 0.19 | 0 | 0
| 30/08/2023 09:00 | HPC W15B HS2 toilet - skate crossword, clay | [7 empty] | 0.14 | 0.23 | 2 | 3
| 30/08/2023 09:15 | HPC W15B 3 Story - hardback landlady large - parent | [7 empty] | 0.18 | 0.39 | 0 | 0
| 30/08/2023 09:45 | HPC W13 heat sink lift - suiting gear slightly | [7 empty] | 0.19 | 0.21 | 1 | 0
| 2023-08-30 10:15 | HPC W11 Outfall lift balfor beatty - regress outreach vote | [7 empty] | 0.23 | 0.49 | 0 | 0
|  | Mean | 0.17274 | 0.23116 | 0.02 | 0.0144 | 0.023 | 0.00678 | 0.0152 | 0.3141 | 0.35275
|  | 95th percentile | 0.35 | 0.4 | 0.03 | 0.0305 | 0.08 | 0.0281 | 0.04 | 0.632 | 0.61
|  | Waste (mean) | 0.57579 | 0.77053 | 0.066667 | 0.048 | 0.076667 | 0.0226 | 0.050667 | 1.047 | 1.1758
|  | waste(95th) | 1.1667 | 1.3333 | 0.1 | 0.10167 | 0.26667 | 0.093667 | 0.13333 | 2.1067 | 2.0333
|  | Max waste | 1.8 | 1.9 | 0.7 | 0.63333 | 0.46667 | 0.12333 | 0.4
|  | EQS (long term/mean) |  |  |  | 0.00476 | 1 |  | 0.0068
|  | EQS (short term/95th percentile) | 0.01 | 0.01 | [5 empty] | 0.01 | 0.01
|  | % of recorded values above EQS | 100 | 100 |  | 100 | 0 |  | 100 | 100 | 100

## Potable Waste Test 5
Copper- Test 5 |  | Zinc- Test 5 |  | Free Chlorine- Test 5
Water Depth (m) | 3 | Water Depth (m) | 3 | Water Depth (m) | 3
Flow rate (m3) | 0.07 | Flow rate (m3) | 0.07 | Flow rate (m3) | 0.07
Release conc. (µg/l) | 102 | Release conc. (µg/l) | 140 | Release conc. (µg/l) | 1200
Discharge vol.*Conc (A) | 7.14 | Discharge vol.*Conc (A) | 9.8 | Discharge vol.*Conc (A) | 84
Background conc. (µg/l) | 3.95 | Background conc. (µg/l) | 3.035 | Background conc. (µg/l) | 0
EQS | 4.76 | EQS | 6.8 | EQS | 10
EQS - Background conc. (B) | 0.81 | EQS - Background conc. (B) | 3.765 | EQS - Background conc. (B) | 10
EVF (A/B) | 8.8148 | EVF (A/B) | 2.6029 | EVF (A/B) | 8.4
<3? | NO | <3? | YES | <3? | NO

## CeTP copper Test 5
Copper |  |  |  | Chlorine
| value | unit | source |  | value | unit | source
concentration in effluent - pre IX | 10000 | µg/l | H&E Env design summary (100975779) | concentration in effluent - pre IX | 500 | µg/l | H&E Env design summary (100975779)
Concentraton after 1 IX column (99% removal) | 100 | µg/l | H&E Env design summary (100975779) | Concentraton after 1 IX column (99% removal) | 5 | µg/l | H&E Env design summary (100975779)
Cocntration after 2 IX columns (99% removal) | 1 | µg/l | H&E Env design summary (100975779) | Cocntration after 2 IX columns (99% removal) | 0.05 | µg/l | H&E Env design summary (100975779)
flow rate | 70 | l/s |  | flow rate | 70 | l/s
Flow rate | 0.07 | m3/s |  | Flow rate | 0.07 | m3/s
Release conc. (µg/l) | 100 |  |  | Release conc. (µg/l) | 5
Discharge vol.*Conc (A) | 7 |  |  | Discharge vol.*Conc (A) | 0.35
Background conc. | 3.95 |  |  | Background conc. | 0
EQS | 4.76 |  |  | EQS | 10
EQS - Background conc. (B) | 0.81 |  |  | EQS - Background conc. (B) | 10
EVF (A/B) | 8.642 |  |  | EVF (A/B) | 0.035
<3? | NO |  |  | <3? | YES

## In combination effects
Activity | Flow rates (l/s) | Copper Max concentration (µg/l) | Zinc Max Concentration (µg/l)
E2 | 20 | 221 | 1642.15
F | 0.57 | 68 | 189
H | 30 | 221 | 1642.15
I | 70 | 102 | 140
Final mix | 120.57 | 151.1882 | 763.1685
Dilution factors |  | 186.6521 | 202.7008