## 1. H1 test
|  |  |  | 6000m3/day | 3731m3/day
H1 screening tests
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine EQS - Long term (AA,) ug/l | Marine EQS - Short term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?) | Comments
Ammonia (un-ionised) | 129250 | 224000 | 5 years data (2015-2019) | 0.069 | 0.043 | 20 |  | 20ug/l as an AA EQS was used in previous H1 assessment. The EA EQS spreadsheets state 21ug/l as the appropriate EQS. Left as 20ug/l as more stringent | fail | N/A
TOC | 67273 | 113800 | 5 years data (2015-2019) | 0.069 | 0.043 |  |  | Previous EA advice: An assessment of parameters without an EQS should be done for any chemicals that the effluent is 'liable to contain' that don’t have an EQS associated with it. TOC is not a chemical and not considered a priority hazardous substance etc. Not assessed further.
Benzene | 325 | 900 | 5 years data (2015-2019) | 0.069 | 0.043 | 8 | 50 | EQS as per EA guidance. | fail | fail
Cadmium and its compounds (< 40 mg/l Ca CO3) | 0.151 | 0.42 | 5 years data (2015-2019) | 0.069 | 0.043 | 0.2 | 0.44 | EA guidance/EQS spreadsheet states that a MAC EQS is not applicable for cadmium and an annual average EQS of 0.2ug/l is applicable. The previous H1 assessment stated a MAC EQS of 0.44ug/l which has been included, however based on latest guidance could be remove and is thought to be not applicable. Cadmium still passes Test 1 regardless. | pass | pass
Mercury | 0.163 | 0.3 | 5 years data (2015-2019) | 0.069 | 0.043 |  | 0.07 | EQS as per EA guidance. | N/A | fail
BOD | 66501.7 | 95875.8 | Annual data - 2019 | 0.069 | 0.043 |  |  | Not usually screened against in H1 - See Annex D2, Sanitary determinand. However, Annex D2 does not cover the assessment of BOD to Trac Waters. Given discharge to a tidal stretch of water there is likely to be adequate dilution and dispersion once the effluent discharge meets the main River Tees stretch. Previous EA advice: The assessment of parameters without an EQS should be done for any chemicals that the effluent is 'liable to contain' that don’t have an EQS associated with it. BOD is not a chemical and not considered a priority hazardous substance etc. Not assessed further.
Nitrogen (dissolved) | 124863.5 | 266636.3 | Annual data - 2019 | 0.069 | 0.043 |  |  | Not to be screened against in H1 - See Annex D2. Sanitary determinand. Previous EA advice: The assessment of parameters without an EQS should be done for any chemicals that the effluent is 'liable to contain' that don’t have an EQS associated with it. Nitrogen is not a chemical and not considered a priority hazardous substance etc. Not assessed further.
Nitrobenzene | 6236.8 | 10699.9 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
2,4-dinitrophenol | 1126.1 | 1700 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
2,6-dinitrophenol | 550.7 | 1737.8 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
2-nitrophenol | 317.5 | 703 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
4-nitrophenol | 235.2 | 335.3 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Sulphate | 847608.8 | 2555556.7 | Annual data - 2019 | 0.069 | 0.043 | 400000 |  | EA guidance states that marine EQS's are not applicable for Sulphate. In the absence of any other standard, the substance has been compared against freshwater standard of 400000ug/l but will be highly conservative. | fail | N/A
Formate | 3780.1 | 11550.5 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Oxalate | 47396.2 | 87319 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Aminobenzene (Aniline) | 9390.7 | 23681.3 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Picric acid | 5248.9 | 6961.5 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Cyclohexylamine | 1007.8 | 2421.1 | Annual data - 2019 | 0.069 | 0.043 |  |  | No EQS, Alternative values such as PNEC to be obtained, see tab 2. | See tab 2 for further details
Phenol (95%ile) | 115.1 | 292.1 | Annual data - 2019 | 0.069 | 0.043 | 7.7 | 46 | EQS as per EA guidance. | fail | fail
Chromium VI (95%ile) (dissolved) | 52 | 176 | Annual data - 2019 | 0.069 | 0.043 | 0.6 | 32 | EQS as per EA guidance. | fail | fail
Nickel | 88 | 229 | Annual data - 2019 | 0.069 | 0.043 | 8.6 | 34 | EQS as per EA guidance. | fail | fail
Copper | 19 | 175 | Annual data - 2019 | 0.069 | 0.043 | 3.6 |  | EA guidance states an EQS of 3.76ug/l if DOC is less than 1mg/l. If DOC is greater than 1mg/l 3.76 + (2.677 x ((DOC/2) –0.5)) μg/l. Background data for the area shows an average DOC concentration of 7.9mg/l. Therefore the equation for when DOC is above 1mg/l should be used. This calculation equates to an EQS figure of 13.83ug/l. The H1 tool automatically has copper listed as a substance with an EQS of 3.6ug/l. Given this is already a more stringent limit, this would be acceptable to use as a screening threshold and reviewed again if copper does not screen out of the screening test. | fail | N/A
Zinc | 30.1 | 177.1 | Annual data - 2019 | 0.069 | 0.043 | 6.8 |  | EA guidance states is 6.8ug/l. EA guidance states that for Zinc, the concentration should be dissolved plus ambient background concentration. For saltwater, an Ambient Background Concentration of 1.1 µg/l is recommended. The release concentration in the effluent is 29ug/l AA and 176ug/l MAC. When adding background concentration of 1.1ug/l, release concentrations are 30.1ug/l AA and 177.1ug/l. | fail | N/A
SS | 69 | 303 | Annual data - 2019 | 0.069 | 0.043 |  |  | Not generally screened against in H1, assessed via Annex D2 -Sanitary determinand. However Annex D2 not applicable for TRAC waters. Tidal water bodies are characterised for generally having strong tidal flows and the receiving coastal water should have a high capacity for mixing of solids. Upon entering the coastal water bodies suspended solids would be rapidly dispersed. Background data obtained from the EAs WIMS sample point downstream of the Dabholm Gut has an average background concentration of 15mg/l. Discharge from emission point S1 would on average add 0.3mg/l of solids to the Dabholm Gut flowing to the River Tees. Therefore the discharge of suspended solids at relatively low concentrations would be insignificant with respect to the existing background concentrations. Previous EA Advice: the assessment of parameters without an EQS should be done for any chemicals that the effluent is 'liable to contain' that don’t have an EQS associated with it. SS are not a chemical and not considered a priority hazardous substance etc. Not assessed further.
2,4,6-Trinitrophenol |  |  | Annual data - 2019 | 0.069 | 0.043 |  |  | 2,4,6-Trinitrophenol also known as Picric acid. Assessed above under Picric acid.

## 2. Alternative standards
Where a substance does not have a defined EQS, alternative standards have been identified. Please see subsequent tabs for each substance with no set EQS.

## 2.1 Nitrobenzene
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Nitrobenzene | [8 empty] | Nitrobenzene
Long term (AA) | [8 empty] | Long term (AA)
Nitrobenzene | 6236.8 | 10699.9 | Annual data - 2019 | 0.069 | 0.043 | 38 |  | PNEC marine overall = 38 ug/L No sensitivity differences between freshwater and marine organisms. | fail

## 2.2 .2,4-dinitrophenol
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
2,4-dinitrophenol | [8 empty] | 2,4-dinitrophenol
Long term (AA) | [8 empty] | Long term (AA)
2,4-dinitrophenol | 1126.1 | 1700 | Annual data - 2019 | 0.069 | 0.043 | 2.08 |  | PNEC marine = 2.08ug/l From all data it can be concluded that sensitivity between marine and freshwater is comparable. In that case an AF of 100 can be applied on the lowest NOEC from either fw or marine data. Freshwater fish provides the lowest NOEC and therefore PNECmarine will be 2.08 ug/L | fail

## 2.3. 2,6-dinitrophenol
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
2,6-dinitrophenol | [8 empty] | 2,6-dinitrophenol
Long term (AA) | [8 empty] | Long term (AA)
2,6-dinitrophenol | 550.7 | 1737.8 | Annual data - 2021 | 0.069 | 0.043 | 2.08 |  | PNEC marine = 2.08ug/l From all data it can be concluded that sensitivity between marine and freshwater is comparable. In that case an AF of 100 can be applied on the lowest NOEC from either fw or marine data. Freshwater fish provides the lowest NOEC and therefore PNECmarine will be 2.08 ug/L | fail

## 2.4. 2-nitrophenol
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
2,nitrophenol | [8 empty] | 2nitrophenol
Long term (AA) | [8 empty] | Long term (AA)
2-nitrophenol | 317.5 | 703 | Annual data - 2021 | 0.069 | 0.043 | 14 |  | PNEC marine = 14 ug/L No specific marine data mentioned in dossier. An AF of 100 can be applied to the lowest of 3 trophic levels being algae with an EC10 of 1.4 mg/L | fail

## 2.5. 4-nitrophenol
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
4,nitrophenol | [8 empty] | 4 nitrophenol
Long term (AA) | [8 empty] | Long term (AA)
4-nitrophenol | 235.2 | 335.3 | Annual data - 2019 | 0.069 | 0.043 | 2.6 |  | PNEC marine = 2.6 ug/L PNECmarine derived by using an AF of 500 on the lowest NOEC from the Daphnia study | fail

## 2.6. Formate
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Formate | [8 empty] | Formate
Long term (AA) | [8 empty] | Long term (AA)
Formate | 3780.1 | 11550.5 | Annual data - 2019 | 0.069 | 0.043 | 200 |  | PNEC marine value for Formic acid (aquatic organisms, marine) = 200ug/l. Formate is a monocarboxylic acid anion that is the conjugate base of formic acid. In the absence of standards for formate, standards for Formic acid collected. | fail

## 2.7 Oxalate
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Oxalate | [8 empty] | Oxalate
Long term (AA) | [8 empty] | Long term (AA)
Oxalate | 47396.2 | 87319 | Annual data - 2019 | 0.069 | 0.043 | 1.9 |  | PNEC marine = 1.9ug/L For PNEC marine in absence of long-term data an AF of 10000 needs to be applied on the lowest L(E)C50 which is the EC50 for algae. PNEC marine will become 1.9 ug/L. | fail

## 2.8. Aminobenzene (Aniline)
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Aminobenzene (Aniline) | [8 empty] | Aminobenzene (Aniline)
Long terms (AA) | [8 empty] | Long term (AA)
Aminobenzene (Aniline) | 9390.7 | 23681.3 | Annual data - 2022 | 0.069 | 0.043 | 0.12 |  | PNEC marine = 0.12ug/l PNEC marine derived with an AF of 100 on the lowest NOEC for Daphnia. This results in a PNEC of 0.12 ug/L. | fail

## 2.9. Picric acid
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Picric acid | [8 empty] | Picric acid
Long terms (AA) | [8 empty] | Long term (AA)
Picric acid | 5248.9 | 6961.5 | Annual data - 2022 | 0.069 | 0.043 | 28.6 |  | PNEC marine = 28.6 ug/L An AF of 100 can be applied to the lowest NOEC for fish. PNEC marine of 28.6ug/l derived. | fail

## 2.10 Cyclohexylamine
Input data | [8 empty] | Test 1
Substance | Release concentration (ug/l) (AA) | Release concentration (ug/l) (MAC) | Sample data | Discharge volume m3/s (maximum) | Discharge volume m3/s (average) | Marine alternative standard - Long term (AA) ug/l | Marine alternative standard- Short term term (MAC) ug/l | Comment/source | Test 1 (substance less AA EQS?) | Test 1 (substance less MAC EQS?)
Cyclohexylamine | [8 empty] | Cyclohexylamine
Long terms (AA) | [8 empty] | Long term (AA)
Cyclohexylamine | 1007.8 | 2421.1 | Annual data - 2021 | 0.069 | 0.043 | 3.2 |  | PNEC Marine = 3.2 ug/L PNEC marine derived by applying AF 500 on the lowest NOEC from Daphnia as data are available for 2 trophic levels. PNEC marine will be 3.2 ug/L | fail

## Effluent Flow data
| 2019 |  | 2020 |  | 2021
| Average | Max | Average | Max | Average | Max |  | Max | 6000m3/d | 0.06944444 m3/s
January | 3357 | 3603 | 4108 | 4953 | 4405 | 5087 |  | Average | 3731m3/d | 0.04318287 m3/d
February | 3378 | 4130 | 4553 | 5082 | 4299 | 4779
March | 3126 | 3701 | 4338 | 5063 | 2444 | 4996
Apr | 3390 | 3876 | 3700 | 4389 | 1342 | 3840
May | 2850 | 3775 | 3565 | 4430 | 4482 | 4922
June | 2422 | 3547 | 2876 | 3991 | 4111 | 4676
July | 3569 | 4609 | 4061 | 4976 | 3715 | 4778
August | 3821 | 4282 | 4233 | 4957 | 4167 | 4938
September | 3915 | 4667 | 4763 | 5362 | 4052 | 4380
October | 4103 | 4666 | 4640 | 5352 | 3749 | 5527
November | 3562 | 4286 | 4607 | 5658 | 3864 | 4724
December | 3015 | 3712 | 4283 | 4568 | 3451 | 4275
| 3375.6667 |  | 4143.9167 |  | 3673.4167 |  | 3731 | 3731