## Emissions Summary
Source | From ES | Standard | Scaled/calc from BP data | From BP | Derived from generic data
| Units | Boiler (normal) | Boiler (start up) | Fired Heater (start up) | Emergency Generator (3.1 MW output) | Flare (emergency Case 1) | Flare (emergency Case 2) | Flare (emergency Case 3) | Flare (Pilot)
MW thermal | MWth | 71.8693 | 71.8693 | 18.293 | 8.8571
Efficiency |  | 1.4314 | 1.4314
Flowrate (Normal) | kNm³/hr | 72.6 | 72.0256 | 18.3327
Flowrate (design) | kNm³/hr (note 1) | 77.5
Fuel Flowrate | t/h | 4.77 | 5.6366 | 1.4347
Fuel Flowrate | Kg/s | 1.325 | 1.5657 | 0.39852
Temperature | °C | 155 | 259 | 200 | 600 | 1000 | 1000 | 1000 | 1000
Real/Effective stack height | m | 70 | 70 | 35 | 10 | 99.8576 | 97.7045 | 100.6265 | 66.3744
Exhaust Composition
Water | mol % | 29.26 |  | 18.02
Carbon Dioxide | mol % | 2.24 |  | 8.85
Oxygen | mol % | 1.57 |  | 1.64
Nitrogen | mol % | 65.97 |  | 70.62
Argon | mol % | 0.94 |  | 0.87
Ammonia | mol % | By Vendor
NOx | ppmv | By DEC (note 2) |  | By DEC (Note 4)
SO2 | ppmv | Note 3 |  | 1.5 (Note 5)
Diameter - sized to achieve around 15 m/s on normal Op or calculated for flares | m | 1.9 | 1.9 | 0.9 | 0.9 | 11.4952 | 10.7535 | 11.7605 | 0.8688
Exhaust airflow at actual stack conditions | km3/h | 164.5866
Exhaust airflow at actual stack conditions | m3/s | 45.7185 | 46.7098 | 10.5709 | 9.9811 |  |  |  | 1.0227 (0.248 kg/s)
Velocity | m/s | 16.1248 | 16.4745 | 16.6165 | 15.6892 | 20 | 20 | 20 | 20
Reference Oxygen Content (%) |  | 3 | 3 | 3
Reference Emission temperature (deg C) |  | 0
Reference H2O Content (%) |  | 0
NOx emissions Long Term | mg/Nm3 (ELV/BAT) | 75 | 100 | 200
Nox emissions Short Term | mg/Nm3 (ELV/BAT) | 106.25 | 100 | 200
CO emissions | mg/Nm3 (ELV/BAT) | Negligible emissions from hydrogen | 100 | 100
PM emissions | mg/Nm3 (ELV/BAT) | Negligible emissions from Hydrogen/Nat gas
Ammonia | mg/Nm3 (ELV/BAT) | 3 | No SCR at start up | No SCR at start up
SO2 | mg/Nm3 (ELV/BAT) | Negligible emissions from Hydrogen/Nat gas |  | 3.9
NOx | g/kW-hr (Tier 2) |  |  |  | 6.4
PM | g/kW-hr (Tier 2) |  |  |  | 0.2
CO | g/kW-hr (Tier 2) |  |  |  | 3.5
NOx emissions Long-term | g/s | 1.6146 | 2.0007 | 1.0185 | 5.5111 | 21.9725 | 19.2287 | 22.9986 | 0.010448
NOx emissions Short-term | g/s | 2.2873 | 2.0007 | 1.0185 | 5.5111 | 21.9725 | 19.2287 | 22.9986
CO emissions short-term | g/s |  | 2.0007 | 0.50924 | 3.0139 | 100.1686 | 87.6603 | 104.8467 | 0.04763
PM emissions | g/s |  |  |  | 0.17222 | 8.7244 | 7.6349 | 9.1318 | 0.00085948
Ammonia | g/s | 0.064583
SO2 | g/s |  |  | 0.01986

## Boiler - Dry gas calc
Molar Gas Calc Sheet
Unit 1 - Boiler - Normal Operation
Data and Physical Properties
|  |  | xi | Mi | wi | wt% | Gi | ρi | Qi | ρi
| Composition Material | Mol% | Mol Fraction | Molar Mass | Mass Fraction | Mass % | Component Mass Flow | Density @T K | Volumetric Flow Rate@T K | Concentration |  | dry gas volume % | Volume dry ref O2, 273K
|  |  | Gi: kg/s; ρi: kg/m3; Qi: m3/s; ρi: kg/m3 | mg/m3 |  | Nm3/s
| O2 | 1.57 | 0.015703 | 31.999 | 0.019613 | 1.9613 | 0 | 0.91063 | 0 | #DIV/0! | #DIV/0! | 2.22
| SO2 | 0 | 0 | 64.0638 | 0 | 0 | 0 | 1.8231 | 0 | #DIV/0! | #DIV/0!
| CO2 | 2.24 | 0.022404 | 44.0095 | 0.038485 | 3.8485 | 0 | 1.2524 | 0 | #DIV/0! | #DIV/0!
| Ar | 0.94 | 0.0094019 | 39.948 | 0.01466 | 1.466 | 0 | 1.1368 | 0 | #DIV/0! | #DIV/0!
| N2 | 65.97 | 0.65983 | 28.0134 | 0.72146 | 72.1457 | 0 | 0.7972 | 0 | #DIV/0! | #DIV/0!
| H2O | 29.26 | 0.29266 | 18.0153 | 0.20579 | 20.5785 | 0 | 0.51268 | 0 | #DIV/0! | #DIV/0!
| Total | 99.98 | 1 | 25.6205 | 1 | 100 | 0 |  | 0 | #DIV/0! | #DIV/0! | 0 | 0
P | Pressure | 1.013 | xi: bara
G | Mass Flowrate |  | xi: Kg/s; wi: 0; wt%: kg/hr
d | Pipe diameter | 1900 | xi: mm; Mi: 1.9; wi: m
T | Temperature | 155 | xi: C; Mi: 428.15; wi: K
A | Area of Pipe | 2.8353 | bar: xi
ui | Velocity | 0 | xi: m/s
| reference O2 | 3 | bar: xi
| vol flow at T | 0 | Am3/s |  | 0 | Am3/hr | #DIV/0! |  | 0 | Nm3/hr to T only
| normalised flow at ref | 0 | xi: Nm3/s; wi: 0; wt%: Nm3/hr

## Boiler StartUp Calculations
| Scenario | H2T
| Data | F-101 Steam Boiler Package BH001-PR-DAT-544-00037.pdf
| Emission Source | Boiler
Inputs
Key Calculated Values
Stack Physical Parameters
| Parameter | Value | Units | Factor
| Stack Name | Boiler
Emission Points
Coordinates (X, Y)
| Release Height | 70 | m
| Diameter of Equivalent Area | 1.9 | m
| Fuel Flow Rate | 5.6366 | tonne/hour | The maximum is determined by the formula as (0.081/1000)*(PI()*(C16/2)^2)*3600
Step 1 | Enter Gas Fuel Compostion
| Component | Formula | Molecular weight MWT | Component Mole Percentage Cmol | Relative Weight Wtr = Cmol/100*MWT | Component Weight Percentage Cwt = Wtr/MWTave | Gross Heating Value (Higher Heating Value) (GJ/t) | Net heating Value (Lower Heating Value) (GJ/t) | HHV*Cwt | LHV*Cwt | Fuel Molecular Carbon Content | Fuel Molecular Hydrogen Content | Component Carbon (Ratio to Fuel) | Component Hydrogen (Ratio to Fuel) | Comb. O2 required (Ratio to Fuel) | Comb. Air required (Ratio to Fuel) | Flue Molecular CO2 (Ration to Fuel) | Flue Molecular H2O (Ratio to Fuel) | LHV (J/g-mol)
| Nitrogen | N2 | 28 | 3.64 | 1.0192 | 5.881% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | #VALUE!
| Water | H2O | 18 | 0 | 0 | 0% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0 | #VALUE!
| Carbon Dioxide | CO2 | 44 | 0.77 | 0.3388 | 1.955% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0077 | --- | #VALUE!
| Hydrogen Sulphide | H2S | 34 | 0 | 0 | 0% | 35.06 | 31.56 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1073040
| Methane | CH4 | 16 | 91.79 | 14.6864 | 84.74% | 55.5785 | 50.0368 | 47.097 | 42.4011 | 1 | 4 | 0.9179 | 3.6716 | 1.8358 | 8.7419 | 0.9179 | 1.8358 | 800589.5357
| Ethane | C2H6 | 30 | 3 | 0.9 | 5.193% | 51.9418 | 47.5079 | 2.6973 | 2.4671 | 2 | 6 | 0.06 | 0.18 | 0.105 | 0.5 | 0.06 | 0.09 | 1425235.8491
| Propane | C3H8 | 44 | 0.59 | 0.2596 | 1.498% | 50.37 | 46.3378 | 0.75448 | 0.69408 | 3 | 8 | 0.0177 | 0.0472 | 0.0295 | 0.14048 | 0.0177 | 0.0236 | 2038863.2708
| Butanes | C4H10, Isobutane, methylpropane | 58 | 0.14 | 0.0812 | 0.4685% | 49.4711 | 45.6469 | 0.23178 | 0.21386 | 4 | 10 | 0.0056 | 0.014 | 0.0091 | 0.043333 | 0.0056 | 0.007 | 2647518.3076
|  | C4H10, n-Butane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
| Pentanes | C5H12, Isopentane, methylbutane, 2-methylbutane | 72 | 0.04 | 0.0288 | 0.1662% | 48.9348 | 45.2638 | 0.081317 | 0.075217 | 5 | 12 | 0.002 | 0.0048 | 0.0032 | 0.015238 | 0.002 | 0.0024 | 3258997.0501
|  |  | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
| Hexanes | C6H14 | 86 | 0.02 | 0.0172 | 0.09924% | 48.7106 | 45.1029 | 0.048342 | 0.044761 | 6 | 14 | 0.0012 | 0.0028 | 0.0019 | 0.0090476 | 0.0012 | 0.0014 | 3878847.7366
| Benzene | C6H6 | 78 | 0 | 0 | 0% | 42.2791 | 40.572 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0
| Heptanes | C7H16 | 100 | 0 | 0 | 0% | 48.4733 | 44.9269 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | C7H8 | 92 | 0 | 0 | 0% | 42.8689 | 40.9392 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0
| C8+ | C8H18 | 114 | 0 | 0 | 0% | 48.2902 | 44.7899 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0
| Insert components above this row | C6H14 | 86 |  | 0 | 0% | 48.7106 | 45.1029 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3878847.7366
| Total gas | --- | --- | 99.99 | 17.3312 | 100% | --- | --- | 50.9102 | 45.896 | --- | --- | 1.0044 | 3.9204 | 1.9845 | 9.45 | 1.0044 | 1.9602
| NMVOCs only | --- | --- | 3.79 | --- | 7.425% | --- | --- | --- | --- | --- | --- | --- | --- | ---
Note: If the analysis includes other compounds, add to species of closest molecular weight above.
Calculated Properties from Gas Fuel Composition
| Parameter | Value | Units | Factor | 15 | C
| Fuel Gas Molecular Weight (MWTave) | 17.3329 | g/mol | 0.73305 | kg/Sm3 |  | #REF! | [7 empty] | 27.8315
| Total Gas Mass HHV | 50.9102 | GJ/tonne | 37.3199 | MJ/Sm3
| Total Gas Mass LHV | 45.896 | GJ/tonne | 33.6442 | MJ/Sm3
Step 2 | Calculated Properties from Gas Fuel Composition
2.1 To calculate stoichiometric waste gas flows
Stoichiometric waste gas (wet)
| Wsw = SUM Vp = | 10.4301 | m3/m3 gas burnt
Stoichiometric waste gas (dry)
| Wsd = SUM Vp -Vh2o = | 8.4699 | m3/m3 gas burnt
| 2.2 To calculate waste gas flows with excess air present |  |  |  | NB Excess air can be estimated from
[5 empty] | O2 measurements in dry flue gas: |  | O2 % = | 3 | % | Wsd=(21-%O2)/21*Wad
| Excess air |  | 14.9381 | % |  |  | Ea % = | 14.9381 | % | Wsd=(21-%O2)/21*(Wsd+Ea*Vs)
| Ea = | Va-Vs | 0.14938 | [6 empty] | Wsd+Ea*Vs=Wsd*21/(21-%O2)
|  | Vs | [7 empty] | Ea*Vs=Wsd/(21-%O2)*[21-(21-%O2)]
| Va = actual air | [8 empty] | Ea*Vs=Wsd/(21-%O2)*%O2
| Vs = Stoichiometric air | 9.45 | m3/m3 gas burnt | [6 empty] | Ea=%O2/(21-%O2)*(Wsd/Vs)
Actual Air Va
| Va = Vs(1+Ea) | 10.8617 | m3/m3 gas burnt
Actual waste gas Wa:
| Waw (wet) =Wsw +Ea*Vs | 11.8418 | m3/m3 gas burnt |  |  |  | @ CO2 % | 8.547%
| Wad (dry) =Wsd +Ea*Vs | 9.8816 | m3/m3 gas burnt | @ O2 % | 3 | Measured O2 | @ CO2 % | 10.24%
10.16%
| Reported at reference O2%, dry | 9.8816 | m3/m3 gas burnt | @ O2 % | 3 | Reference O2
2.3 To calculate waste gas flow rate based on natural gas consumption rate
| Assumed fuel usage (JMcW) | 6208.703 | GJ/day | 55815.8644
|  | 258.696 | GJ/hr
| Calorific value | 0.033644 | GJ/m3
|  | 7689.165 | Sm3 gas/hr | at | 15 | C
| Fuel flow | 7288.8961 | Nm3 gas/hr | at | 0 | C | Actual air flow | 79169.4384 | Nm3 air/hr
| Waste gas flow rate | Normal (Reference O2, dry, 0 C)
|  | 9.8816 | m3/m3 gas burnt
|  | 72025.5913 | Nm3/hour | 51 | mg NOx / Nm3 | 1.0204 | g Nox / s
|  | 20.0071 | Nm3/s | 100 | mg CO / Nm3 | 2.0007 | g CO / s
|  | Actual | (measured or calculated conditions)
|  | 11.8418 | m3/m3 gas burnt
| Temp (K) | 532.15 | K |  | (temp | 259 | oC)
|  | 168155.2805 | m3/hour |  | (moisture | 16.5533 | %H2O) | to check
|  | 46.7098 | m3/s |  | (O2 | 3 | %O2)
fuel usuage for each boiler
|  | 0.07186 | gj/s | 55815.8644 | MW
|  | 4.3116 | gj/min
|  | 258.696 | gj/hr | 55815.8644 | MWh
|  | 6208.703 | gj/day | 1339580.7458 | MWh/day
|  | 2266176.6056 | gj/year | 488946972.2034 | MWh/annum
Note on E17: Chuansen Ren: This maximum rate is determined according to an academic paper: Bubbico R., Dusserre G., Mazzarotta B., 2016, Calculation of the flame size from burning liquid pools, Chemical Engineering Transactions, 53, 67-72 DOI: 10.3303/CET1653012
Note on F38: Chuansen Ren: Average Molecular Weight MWTave = ∑Wtr

## FH StartUp Calculations
| Scenario | H2T
| Data | F-201 Startup Fired Heater BH001-PR-DAT-544-00035.pdf
| Emission Source | Fired Heater
Inputs
Key Calculated Values
Stack Physical Parameters
| Parameter | Value | Units | Factor
| Stack Name | Fired Heater
Emission Points
Coordinates (X, Y)
| Release Height | 35 | m
| Diameter of Equivalent Area | 0.9 | m
| Fuel Flow Rate | 1.4347 | tonne/hour | The maximum is determined by the formula as (0.081/1000)*(PI()*(C16/2)^2)*3600
Step 1 | Enter Gas Fuel Compostion
| Component | Formula | Molecular weight MWT | Component Mole Percentage Cmol | Relative Weight Wtr = Cmol/100*MWT | Component Weight Percentage Cwt = Wtr/MWTave | Gross Heating Value (Higher Heating Value) (GJ/t) | Net heating Value (Lower Heating Value) (GJ/t) | HHV*Cwt | LHV*Cwt | Fuel Molecular Carbon Content | Fuel Molecular Hydrogen Content | Component Carbon (Ratio to Fuel) | Component Hydrogen (Ratio to Fuel) | Comb. O2 required (Ratio to Fuel) | Comb. Air required (Ratio to Fuel) | Flue Molecular CO2 (Ration to Fuel) | Flue Molecular H2O (Ratio to Fuel) | LHV (J/g-mol)
| Nitrogen | N2 | 28 | 3.64 | 1.0192 | 5.881% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | #VALUE!
| Water | H2O | 18 | 0 | 0 | 0% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0 | #VALUE!
| Carbon Dioxide | CO2 | 44 | 0.77 | 0.3388 | 1.955% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0077 | --- | #VALUE!
| Hydrogen Sulphide | H2S | 34 | 0 | 0 | 0% | 35.06 | 31.56 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1073040
| Methane | CH4 | 16 | 91.79 | 14.6864 | 84.74% | 55.5785 | 50.0368 | 47.097 | 42.4011 | 1 | 4 | 0.9179 | 3.6716 | 1.8358 | 8.7419 | 0.9179 | 1.8358 | 800589.5357
| Ethane | C2H6 | 30 | 3 | 0.9 | 5.193% | 51.9418 | 47.5079 | 2.6973 | 2.4671 | 2 | 6 | 0.06 | 0.18 | 0.105 | 0.5 | 0.06 | 0.09 | 1425235.8491
| Propane | C3H8 | 44 | 0.59 | 0.2596 | 1.498% | 50.37 | 46.3378 | 0.75448 | 0.69408 | 3 | 8 | 0.0177 | 0.0472 | 0.0295 | 0.14048 | 0.0177 | 0.0236 | 2038863.2708
| Butanes | C4H10, Isobutane, methylpropane | 58 | 0.14 | 0.0812 | 0.4685% | 49.4711 | 45.6469 | 0.23178 | 0.21386 | 4 | 10 | 0.0056 | 0.014 | 0.0091 | 0.043333 | 0.0056 | 0.007 | 2647518.3076
|  | C4H10, n-Butane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
| Pentanes | C5H12, Isopentane, methylbutane, 2-methylbutane | 72 | 0.04 | 0.0288 | 0.1662% | 48.9348 | 45.2638 | 0.081317 | 0.075217 | 5 | 12 | 0.002 | 0.0048 | 0.0032 | 0.015238 | 0.002 | 0.0024 | 3258997.0501
|  |  | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
| Hexanes | C6H14 | 86 | 0.02 | 0.0172 | 0.09924% | 48.7106 | 45.1029 | 0.048342 | 0.044761 | 6 | 14 | 0.0012 | 0.0028 | 0.0019 | 0.0090476 | 0.0012 | 0.0014 | 3878847.7366
| Benzene | C6H6 | 78 | 0 | 0 | 0% | 42.2791 | 40.572 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0
| Heptanes | C7H16 | 100 | 0 | 0 | 0% | 48.4733 | 44.9269 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | C7H8 | 92 | 0 | 0 | 0% | 42.8689 | 40.9392 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0
| C8+ | C8H18 | 114 | 0 | 0 | 0% | 48.2902 | 44.7899 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0
| Insert components above this row | C6H14 | 86 |  | 0 | 0% | 48.7106 | 45.1029 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3878847.7366
| Total gas | --- | --- | 99.99 | 17.3312 | 100% | --- | --- | 50.9102 | 45.896 | --- | --- | 1.0044 | 3.9204 | 1.9845 | 9.45 | 1.0044 | 1.9602
| NMVOCs only | --- | --- | 3.79 | --- | 7.425% | --- | --- | --- | --- | --- | --- | --- | --- | ---
Note: If the analysis includes other compounds, add to species of closest molecular weight above.
Calculated Properties from Gas Fuel Composition
| Parameter | Value | Units | Factor | 15 | C
| Fuel Gas Molecular Weight (MWTave) | 17.3329 | g/mol | 0.73305 | kg/Sm3 |  | #REF! | [7 empty] | 27.8315
| Total Gas Mass HHV | 50.9102 | GJ/tonne | 37.3199 | MJ/Sm3
| Total Gas Mass LHV | 45.896 | GJ/tonne | 33.6442 | MJ/Sm3
Step 2 | Calculated Properties from Gas Fuel Composition
2.1 To calculate stoichiometric waste gas flows
Stoichiometric waste gas (wet)
| Wsw = SUM Vp = | 10.4301 | m3/m3 gas burnt
Stoichiometric waste gas (dry)
| Wsd = SUM Vp -Vh2o = | 8.4699 | m3/m3 gas burnt
| 2.2 To calculate waste gas flows with excess air present |  |  |  | NB Excess air can be estimated from
[5 empty] | O2 measurements in dry flue gas: |  | O2 % = | 3 | % | Wsd=(21-%O2)/21*Wad
| Excess air |  | 14.9381 | % |  |  | Ea % = | 14.9381 | % | Wsd=(21-%O2)/21*(Wsd+Ea*Vs)
| Ea = | Va-Vs | 0.14938 | [6 empty] | Wsd+Ea*Vs=Wsd*21/(21-%O2)
|  | Vs | [7 empty] | Ea*Vs=Wsd/(21-%O2)*[21-(21-%O2)]
| Va = actual air | [8 empty] | Ea*Vs=Wsd/(21-%O2)*%O2
| Vs = Stoichiometric air | 9.45 | m3/m3 gas burnt | [6 empty] | Ea=%O2/(21-%O2)*(Wsd/Vs)
Actual Air Va
| Va = Vs(1+Ea) | 10.8617 | m3/m3 gas burnt
Actual waste gas Wa:
| Waw (wet) =Wsw +Ea*Vs | 11.8418 | m3/m3 gas burnt |  |  |  | @ CO2 % | 8.547%
| Wad (dry) =Wsd +Ea*Vs | 9.8816 | m3/m3 gas burnt | @ O2 % | 3 | Measured O2 | @ CO2 % | 10.24%
10.16%
| Reported at reference O2%, dry | 9.8816 | m3/m3 gas burnt | @ O2 % | 3 | Reference O2
2.3 To calculate waste gas flow rate based on natural gas consumption rate
| Assumed fuel usage (JMcW) | 1580.3072 | GJ/day | 55815.8644
|  | 65.8461 | GJ/hr
| Calorific value | 0.033644 | GJ/m3
|  | 1957.1306 | Sm3 gas/hr | at | 15 | C
| Fuel flow | 1855.2498 | Nm3 gas/hr | at | 0 | C | Actual air flow | 20151.0739 | Nm3 air/hr
| Waste gas flow rate | Normal (Reference O2, dry, 0 C)
|  | 9.8816 | m3/m3 gas burnt
|  | 18332.7436 | Nm3/hour | 51 | mg NOx / Nm3 | 0.25971 | g Nox / s
|  | 5.0924 | Nm3/s | 100 | mg CO / Nm3 | 0.50924 | g CO / s
|  | Actual | (measured or calculated conditions)
|  | 11.8418 | m3/m3 gas burnt
| Temp (K) | 473.15 | K |  | (temp | 200 | oC)
|  | 38055.3675 | m3/hour |  | (moisture | 16.5533 | %H2O) | to check
|  | 10.5709 | m3/s |  | (O2 | 3 | %O2)
fuel usuage for each boiler
|  | 0.018291 | gj/s | 55815.8644 | MW
|  | 1.0974 | gj/min
|  | 65.8461 | gj/hr | 55815.8644 | MWh
|  | 1580.3072 | gj/day | 1339580.7458 | MWh/day
|  | 576812.1295 | gj/year | 488946972.2034 | MWh/annum
Note on E17: Chuansen Ren: This maximum rate is determined according to an academic paper: Bubbico R., Dusserre G., Mazzarotta B., 2016, Calculation of the flame size from burning liquid pools, Chemical Engineering Transactions, 53, 67-72 DOI: 10.3303/CET1653012
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TBC
Note on E31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TBC
Note on F38: Chuansen Ren: Average Molecular Weight MWTave = ∑Wtr

## Flare Calculations C1
| Scenario | H2T
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf
| Emission Source | Flare Case1
Inputs
Key Calculated Values
Stack Physical Parameters
| Parameter | Value | Units | Factor
Stack Name
Emission Points
Coordinates (X, Y)
| Release Height | 65 | m
| Diameter of Equivalent Area | 0.9 | m
| Fuel Flow Rate | 186.45 | tonne/hour | The maximum is determined by the formula as (0.081/1000)*(PI()*(C16/2)^2)*3600
Step 1 | Enter Gas Fuel Compostion
| Component | Formula | Molecular weight MWT | Component Mole Percentage Cmol | Relative Weight Wtr = Cmol/100*MWT | Component Weight Percentage Cwt = Wtr/MWTave | Gross Heating Value (Higher Heating Value) (GJ/t) | Net heating Value (Lower Heating Value) (GJ/t) | HHV*Cwt | LHV*Cwt | Fuel Molecular Carbon Content | Fuel Molecular Hydrogen Content | Component Carbon (Ratio to Fuel) | Component Hydrogen (Ratio to Fuel) | Comb. O2 required (Ratio to Fuel) | Comb. Air required (Ratio to Fuel) | Flue Molecular CO2 (Ration to Fuel) | Flue Molecular H2O (Ratio to Fuel) | LHV (J/g-mol)
| Nitrogen | N2 | 28 | 0.19 | 0.0532 | 0.4227% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | #VALUE!
| Water | H2O | 18 | 0.45 | 0.081 | 0.6436% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0045 | #VALUE!
| Carbon Dioxide | CO2 | 44 | 24.48 | 10.7712 | 85.58% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.2448 | --- | #VALUE!
| Hydrogen Sulphide | H2S | 34 | 0 | 0 | 0% | 35.06 | 31.56 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1073040
| Methane | CH4 | 16 | 0.5 | 0.08 | 0.6356% | 55.5785 | 50.0368 | 0.35328 | 0.31806 | 1 | 4 | 0.005 | 0.02 | 0.01 | 0.047619 | 0.005 | 0.01 | 800589.5357
| Ethane | C2H6 | 30 | 0 | 0 | 0% | 51.9418 | 47.5079 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1425235.8491
| Propane | C3H8 | 44 | 0 | 0 | 0% | 50.37 | 46.3378 | 0 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2038863.2708
| Butanes | C4H10, Isobutane, methylpropane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
|  | C4H10, n-Butane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
| Pentanes | C5H12, Isopentane, methylbutane, 2-methylbutane | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
|  |  | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
| Hexanes | C6H14 | 86 | 0 | 0 | 0% | 48.7106 | 45.1029 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3878847.7366
| Benzene | C6H6 | 78 | 0 | 0 | 0% | 42.2791 | 40.572 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3164618.6441
| Heptanes | C7H16 | 100 | 0 | 0 | 0% | 48.4733 | 44.9269 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 4492685.2289
| Toluene | C7H8 | 92 | 0 | 0 | 0% | 42.8689 | 40.9392 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 3766404.9269
| C8+ | C8H18 | 114 | 0 | 0 | 0% | 48.2902 | 44.7899 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5106048.4372
| Hydrogen | H2 | 2 | 73.97 | 1.4794 | 11.75% | 141.7 | 120 | 16.6564 | 14.1056 | 0 | 2 | 0 | 1.4794 | 0.36985 | 1.7612 | 0 | 0.7397 | 240000
| Carbon Monoxide | CO | 28 | 0.3 | 0.084 | 0.6674% | 10.16 | 10.16 | 0.067811 | 0.067811 | 1 | 0 | 0.003 | 0 | 0.003 | 0.014286 | 0.003 | 0 | 284480
| Argon | Ar | 40 | 0.06 | 0.024 | 0.1907% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Methanol | CH₃OH | 32 | 0.04 | 0.0128 | 0.1017% | 23 | 19.9 | 0.023392 | 0.020239 | 1 | 4 | 0.0004 | 0.0016 | 0.0008 | 0.0038095 | 0.0004 | 0.0008 | 636800
| Insert components above this row | C6H14 | 86 |  | 0 | 0% |  |  | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total gas | --- | --- | 99.99 | 12.5856 | 100% | --- | --- | 17.1009 | 14.5118 | --- | --- | 0.0084 | 1.501 | 0.38365 | 1.8269 | 0.0084 | 0.7505
| NMVOCs only | --- | --- | 74.37 | --- | 12.71% | --- | --- | --- | --- | --- | --- | --- | --- | ---
Note: If the analysis includes other compounds, add to species of closest molecular weight above.
Calculated Properties from Gas Fuel Composition
| Parameter | Value | Units | Factor | 15 | C
| Fuel Gas Molecular Weight (MWTave) | 12.5869 | g/mol | 0.53233 | kg/Sm3 |  | 135623.0998 | [7 empty] | 26.5762
| Total Gas Mass HHV | 17.1009 | GJ/tonne | 9.1033 | MJ/Sm3
| Total Gas Mass LHV | 14.5118 | GJ/tonne | 7.725 | MJ/Sm3
Step 2 | Calculated Properties from Gas Fuel Composition
2.1 To calculate stoichiometric waste gas flows
Stoichiometric waste gas (wet)
| Wsw = SUM Vp = | 2.2022 | m3/m3 gas burnt
Stoichiometric waste gas (dry)
| Wsd = SUM Vp -Vh2o = | 1.4472 | m3/m3 gas burnt
| 2.2 To calculate waste gas flows with excess air present |  |  |  | NB Excess air can be estimated from
[5 empty] | O2 measurements in dry flue gas: |  | O2 % = | 0.05 | % | Wsd=(21-%O2)/21*Wad
| Excess air |  | 0.18905 | % |  |  | Ea % = | 0.18905 | % | Wsd=(21-%O2)/21*(Wsd+Ea*Vs)
| Ea = | Va-Vs | 0.0018905 | [6 empty] | Wsd+Ea*Vs=Wsd*21/(21-%O2)
|  | Vs | [7 empty] | Ea*Vs=Wsd/(21-%O2)*[21-(21-%O2)]
| Va = actual air | [8 empty] | Ea*Vs=Wsd/(21-%O2)*%O2
| Vs = Stoichiometric air | 1.8269 | m3/m3 gas burnt | [6 empty] | Ea=%O2/(21-%O2)*(Wsd/Vs)
Actual Air Va
| Va = Vs(1+Ea) | 1.8304 | m3/m3 gas burnt
Actual waste gas Wa:
| Waw (wet) =Wsw +Ea*Vs | 2.2056 | m3/m3 gas burnt |  |  |  | @ CO2 % | 11.48%
| Wad (dry) =Wsd +Ea*Vs | 1.4506 | m3/m3 gas burnt | @ O2 % | 0.05 | Measured O2 | @ CO2 % | 17.45%
0.5791%
| Reported at reference O2%, dry | 1.6883 | m3/m3 gas burnt | @ O2 % | 3 | Reference O2
2.3 To calculate waste gas flow rate based on natural gas consumption rate
| Assumed fuel usage (JMcW) | 64937.1885 | GJ/day | 55815.8644
|  | 2705.7162 | GJ/hr
| Calorific value | 0.007725 | GJ/m3
|  | 350252.9631 | Sm3 gas/hr | at | 15 | C
| Fuel flow | 332020.1175 | Nm3 gas/hr | at | 0 | C | Actual air flow | 607715.8748 | Nm3 air/hr
| Waste gas flow rate | Normal (Reference O2, dry, 0 C)
|  | 1.6883 | m3/m3 gas burnt
|  | 560565.2431 | Nm3/hour | 51 | mg NOx / Nm3 | 7.9413 | g Nox / s
|  | 155.7126 | Nm3/s | 100 | mg CO / Nm3 | 15.5713 | g CO / s
|  | Actual | (measured or calculated conditions)
|  | 2.2056 | m3/m3 gas burnt
| Temp (K) | 1273.15 | K |  | (temp | 1000 | oC)
|  | 3413274.4776 | m3/hour |  | (moisture | 34.2309 | %H2O) | to check
|  | 948.1318 | m3/s |  | (O2 | 0.05 | %O2)
fuel usuage for each boiler
|  | 0.75159 | gj/s | 55815.8644 | MW
|  | 45.0953 | gj/min
|  | 2705.7162 | gj/hr | 55815.8644 | MWh
|  | 64937.1885 | gj/day | 1339580.7458 | MWh/day
|  | 23702073.7867 | gj/year | 488946972.2034 | MWh/annum
Step 3 | Gas Flow Rate (to the Flare) |  |  |  |  | Volume to Mass conversion tool
| Parameter | Value | Units | Factor |  | Gas Volume | Units | Conversion Factor (mass/vol) | Gas Mass | Units
| Mass Flow Rate (M) | 186.45 | tonne/h | Em in 1 hour / Em |  | 0 | sm3 | 0.00053233 | 0 | tonne
| Mass Flow Rate (M) | 51.7917 | kg/s | - |  | 0 | nm3 | 0.00056156 | 0 | tonne
| Mass Flow Rate (M) | 0.051792 | tonne/s | - |  | 0 | scf | 1.5074e-05 | 0 | tonne
| Volumetric Flow Rate (V) | 296.8592 | mmscfd | 1 MMscf = 28.317 103m3 |  | 296.8592 | mmscf | 15.0738 | 4474.8 | tonne
| Volume Flow Rate (V) @15 DegC | 350254.4832 | sm3/hr | -
| Volume Flow Rate (V) @15 DegC | 97.2929 | sm3/s | - |  | Ideal Gas Law Equations PV= nRT | Volume at 0 Deg C | Volume at 25 Deg C | Volume at 15 deg | Units
| Volume Flow Rate (V) @ 0 Deg C | 92.2282 | Nm3/s | Normalised to 0 Deg C |  | Volume (V) | 0.022414 | 0.024466 | 0.023645 | m3/mole
[6 empty] | Pressure (P) | 101325 | 101325 | 101325 | Pa (N/m2)
Step 4 | Efflux Volume Calculations |  |  |  |  | Number of Moles (n) | 1 | 1 | 1 | mole
| Parameter | Value | Units | Factor |  | Gas Constant (R) | 8.3145 | 8.3145 | 8.3145 | JK-1mol-1
| Flow Volume at STD conditions | 97.2929 | sm3/s | - |  | Temperature (T) | 273.15 | 298.15 | 288.15 | kelvins
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Temperature before combustion | 45 | Deg Celcius | -
| Stack Area (Prior to ambient mixing) | 0.63617 | m2 | -
| Efflux Velocity (Prior to Ignition) | 168.8572 | m/s | Vnozzle
| Temp of gas prior to release | 318.15 | Deg K | -
| Flow Volume at Stack (Actual Temp) | 107.4223 | m3/s | -
Step 5 | Heat Release Calculations
| Parameter | Value | Units | Factor
| Total Gas Mass LHV | 14.5118 | GJ/tonne | -
| Total Gas Mass LHV (Hc) | 14511752.1357 | J/kg | -
| Input Energy | 751.5878 | MW | -
| Combustion Efficiency (%) | 99% |  | Was in C128: =(1-59%)/E131
| Total Heat Release (Qc or: Qtot) | 744071951.0664 | Joule/s, W | Em*M
| Heat Release (H) | 177760989.7918 | cal/s | 1 J = 0.23890295762 Cal
| Radiative Loss Factor (f) | 25% | Left for heating | 75%
| Net Heat Release (Qn, ADMS5's Fb) | 558053963.2998 | J/s, W | Hr = (1-f)*H
| Net Heat Release Rate (Hr) | 133320742.3439 | cal/s | 1 J = 0.23890295762 Cal
| Stack Temperature Increase dTs | 2040.818 | K | Assumed Cp = 1012 J/kg.K
| Air Temperature (T) | 288.15 | K | Ambeint air temperature
| Flow at Shrouded Flare (Actual Temp) | 1734.4211 | m3/s | -
| Efflux Velocity (Shrouded Flare) | 2726.3376 | m/s | -
| Momentum Flux (pi * Fm) | 16428.6095 | m4/s2 | elevated, without combustion air, assuming air temperature is 283K.
| Momentum Flux (pi * Fm) | 585045.0214 | m4/s2 | ground, with combustion air, assuming air temperature is 283K |  | https://files.ontario.ca/modelling-open-flares.pdf
Step 6 | Effective Stack Diameter (Pseudo Parameter)
| Parameter | Value | Units | Factor/Equation
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Stack Exit Temperature (Ts) | 1273 | K | US EPA Guidance
| Volume Flow Rate (V) @Stack Exit Temperature Deg 1000 Deg C | 430.0605 | m3/s | V @ 1000 Deg C = V @ 0 Deg C (Nm3)*(Ts/273)
| Exit Velocity (Vs) @ AERMOD DEFAULT VALUE | 20 | m/s | US EPA Guidance
| Exit Velocity (Vs) @ Stack T of 1000 Deg C | 676.0124 | m/s | Vs = V (m3/s) / (PI * D2/4)
| Effective diameter (ds) | 11.4952 | m | (ds) = (0.1066*[(Ts/(T*(Ts-T))*(Hr/Vs)]^0.5) = ds (ft) Iowa DNR
| Effective diameter (ds), AERSCREEN User’s Guide, USEPA | 11.4079 | m | (ds) = 9.88×10−4 × (HR × (1− f))^0.5 EPA
|  | 11.4038 |  |  |  |  | lb/MMBtu to g/GJ
| Effective Stack Height (Pseudo Parameter) | [5 empty] | lb to Kg | 0.45359
| Parameter | Value | Units | Factor/Equation |  |  | lb to g | 453.5924
| Stack height above ground (hs) | 65 | m | - |  |  | Btu to KJ | 1.0551
| Stack height above ground (hs) | 213.2546 | ft | 1 m = 3.280839895 ft |  |  | MMBtu to KJ | 1055056
| Effect flare release height (hsl) | 99.8576 | m | hsl (ft) = (hs + (7.54x10-3) * (Hr^0.478)) IOWA method | 0.0075455 |  | MMBtu to GJ | 1.0551
| Calculation check | 99.8832 | m | hsl (m) =hs +((0.00456)*((Hr/4.1868)^0.478)) IOWA method |  |  | lb/MMBtu to g/GJ | 429.9226
Step 7 | Emission Rates Calculations |  |  |  |  | US AP42 (lb/MMBtu)
| Parameter | Value | Units | Factor |  | Table 13.5-1 (English Units). NOx and Soot; Table 13.5-2 (English Units). CO | [6 empty] | Table 1.4-1
| NOx | 21.9725 | g/s | 0.00042425 |  | Component | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units
| CO | 100.1686 | g/s | 0.0019341 |  | NOX | 29.2347 | g/GJ | 0.068 | lb/MMBtu | 0.00042425 | Mg/Mg | 0.18627 | lb/MMBtu | 190 | lb/MMSCF
| NMVOC | 65.8507 | g/s | 0.0012715 |  | Soot | 11.6079 | g/GJ | 0.027 | lb/MMBtu | 0.00016845 | Mg/Mg | 21.4929 | ug/L exhaust | 0.51 | kg soot/10^3 m3 fuel
| PM10 | 8.7244 | g/s | 0.00016845 |  | CO | 133.276 | g/GJ | 0.31 | lb/MMBtu | 0.0019341 | Mg/Mg | 0.082353 | lb/MMBtu | 84 | lb/MMSCF
| S as H2S | 0 | g/s | 0 |  | https://www3.epa.gov/ttn/chief/ap42/ch13/final/C13S05_02-05-18.pdf
| H2S (5% unburnt) | 0 | g/s | 0
| SO2 (95% burnt S) | 0 | g/s | 0 |  | Acid gas flare Sox EF | [5 empty] | Mg/Mg
| BTEX by venting | 0 | g/s |  |  | Burn Pit Sox EF |  |  |  |  | 0 | Mg/Mg
| BTEX by flaring | 0 | g/s
| Summary Data |  |  | Summary Data
| Scenario | H2T |  | Scenario
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf |  | Data
| Emission Source | Flare Case1 |  | Emission Source
| Emission Source Height (m) | 65 |  | Emission Source Height (m)
| Equivalent Diameter of Area (m) | 0.9 |  | Equivalent Diameter of Area (m)
| Input Fuel Volume Flow Rate (mmscfd) | 296.8592 |  | Input Fuel Volume Flow Rate (mmscfd)
| Input Fuel Mass Flow Rate (t/h) | 186.45 |  | Input Fuel Mass Flow Rate (t/h)
| Input Energy (MWth) | 751.5878 |  | Input Energy (MWth)
| Op 1: Matching Heat and Momentum |  |  | Op 1: Matching Heat and Momentum
| Momentum Flux (ADMS5's Fm) (m4/s2) | 16428.6095 |  | Momentum Flux (ADMS5's Fm) (m4/s2)
| Heat Release (ADMS5's Fb) (MW) | 558.054 |  | Heat Release (ADMS5's Fb) (MW)
| Effective exit gas temperature (K) | 2328.968 |  | Effective exit gas temperature (K)
| Effective exit velocity (m/s) | 74.481 |  | Effective exit velocity (m/s)
| Effective exit diameter (m) | 1.0175 |  | Effective exit diameter (m)
| Op 2: Shrouded Flare or Point Source Approach |  |  | Op 2: Shrouded Flare or Point Source Approach
| Exit gas temperature (K) | 2328.968 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 0.9 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 2726.3376 |  | Exit gas velocity (m/s)
| Op 3: USEPA Flare Approach |  |  | Op 3: USEPA Flare Approach
| Exit gas temperature (K) | 1273 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 11.4079 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 20 |  | Exit gas velocity (m/s)
| All: Emission Rate |  |  | All: Emission Rate
| NOx (g/s) | 21.9725 |  | NOx (g/s) | 4805.5556 | t/h | 17.3
| CO (g/s) | 100.1686 |  | CO (g/s) | 2125 | t/h | 7.65
| NMVOC (g/s) | 65.8507 |  | NMVOC (g/s) | 0 | t/h
| PM10 (g/s) | 8.7244 |  | PM10 (g/s) | 0
| H2S (g/s) | 0 |  | H2S (g/s) | 0
| SO2 (g/s) | 0 |  | SO2 (g/s) | 3369.4444 | t/h | 12.13
Note on E17: Chuansen Ren: This maximum rate is determined according to an academic paper: Bubbico R., Dusserre G., Mazzarotta B., 2016, Calculation of the flame size from burning liquid pools, Chemical Engineering Transactions, 53, 67-72 DOI: 10.3303/CET1653012
Note on F42: Chuansen Ren: Average Molecular Weight MWTave = ∑Wtr
Note on I105: C. Ren: at 15 Deg c
Note on I106: C. Ren: at 0 Deg C
Note on I107: 1 m3 = 35.3 scf
Note on I108: 1 m3 = 35.3 scf
Note on C131: Chuansen Ren: O. Reg. 419/05
Note on C154: Chuansen Ren: Use this in modelling
Note on C156: Chuansen Ren: Don't use this in modelling
Note on C157: Chuansen Ren: Don't use this in modelling either
Note on E161: Chuansen Ren: AP42
Note on E162: Chuansen Ren: AP42
Note on J162: Chuansen Ren: Grade B Factor developed using the higher (gross) heating value of the vent gas
Note on E163: Chuansen Ren: Assume X% overall combustion efficiency, but NMVOC has a lower efficiency than methane
Note on H163: Chuansen Ren: Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on J163: Chuansen Ren: Grade B Soot in concentration values: nonsmoking flares, 0 micrograms per liter (μg/L); lightly smoking flares, 40 μg/L; average smoking flares, 177 μg/L; and heavily smoking flares, 274 μg/L. Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on P163: Chuansen Ren: McEwen & Johnson (2012) https://doi.org/10.1080/10473289.2011.650040
Note on E164: Chuansen Ren: AP42, average smoking flares, g/m3
Note on J164: Chuansen Ren: Poorly

## Flare Calculations C2
| Scenario | H2T
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf
| Emission Source | Flare Case2
Inputs
Key Calculated Values
Stack Physical Parameters
| Parameter | Value | Units | Factor
Stack Name
Emission Points
Coordinates (X, Y)
| Release Height | 65 | m
| Diameter of Equivalent Area | 0.9 | m
| Fuel Flow Rate | 20.46 | tonne/hour | The maximum is determined by the formula as (0.081/1000)*(PI()*(C16/2)^2)*3600
Step 1 | Enter Gas Fuel Compostion
| Component | Formula | Molecular weight MWT | Component Mole Percentage Cmol | Relative Weight Wtr = Cmol/100*MWT | Component Weight Percentage Cwt = Wtr/MWTave | Gross Heating Value (Higher Heating Value) (GJ/t) | Net heating Value (Lower Heating Value) (GJ/t) | HHV*Cwt | LHV*Cwt | Fuel Molecular Carbon Content | Fuel Molecular Hydrogen Content | Component Carbon (Ratio to Fuel) | Component Hydrogen (Ratio to Fuel) | Comb. O2 required (Ratio to Fuel) | Comb. Air required (Ratio to Fuel) | Flue Molecular CO2 (Ration to Fuel) | Flue Molecular H2O (Ratio to Fuel) | LHV (J/g-mol)
| Nitrogen | N2 | 28 | 0.22 | 0.0616 | 2.978% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | #VALUE!
| Water | H2O | 18 | 0 | 0 | 0% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0 | #VALUE!
| Carbon Dioxide | CO2 | 44 | 0 | 0 | 0% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0 | --- | #VALUE!
| Hydrogen Sulphide | H2S | 34 | 0 | 0 | 0% | 35.06 | 31.56 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1073040
| Methane | CH4 | 16 | 0 | 0 | 0% | 55.5785 | 50.0368 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 800589.5357
| Ethane | C2H6 | 30 | 0 | 0 | 0% | 51.9418 | 47.5079 | 0 | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1425235.8491
| Propane | C3H8 | 44 | 0 | 0 | 0% | 50.37 | 46.3378 | 0 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2038863.2708
| Butanes | C4H10, Isobutane, methylpropane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
|  | C4H10, n-Butane | 58 | 0 | 0 | 0% | 49.4711 | 45.6469 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2647518.3076
| Pentanes | C5H12, Isopentane, methylbutane, 2-methylbutane | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
|  |  | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
| Hexanes | C6H14 | 86 | 0 | 0 | 0% | 48.7106 | 45.1029 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3878847.7366
| Benzene | C6H6 | 78 | 0 | 0 | 0% | 42.2791 | 40.572 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3164618.6441
| Heptanes | C7H16 | 100 | 0 | 0 | 0% | 48.4733 | 44.9269 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 4492685.2289
| Toluene | C7H8 | 92 | 0 | 0 | 0% | 42.8689 | 40.9392 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 3766404.9269
| C8+ | C8H18 | 114 | 0 | 0 | 0% | 48.2902 | 44.7899 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5106048.4372
| Hydrogen | H2 | 2 | 99.75 | 1.995 | 96.44% | 141.7 | 120 | 136.6584 | 115.7304 | 0 | 2 | 0 | 1.995 | 0.49875 | 2.375 | 0 | 0.9975 | 240000
| Carbon Monoxide | CO | 28 | 0 | 0 | 0% | 10.16 | 10.16 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284480
| Argon | Ar | 40 | 0.03 | 0.012 | 0.5801% |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Methanol | CH₃OH | 32 | 0 | 0 | 0% | 23 | 19.9 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 636800
| Insert components above this row | C6H14 | 86 |  | 0 | 0% |  |  | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total gas | --- | --- | 100 | 2.0686 | 100% | --- | --- | 136.6584 | 115.7304 | --- | --- | 0 | 1.995 | 0.49875 | 2.375 | 0 | 0.9975
| NMVOCs only | --- | --- | 99.78 | --- | 97.02% | --- | --- | --- | --- | --- | --- | --- | --- | ---
Note: If the analysis includes other compounds, add to species of closest molecular weight above.
Calculated Properties from Gas Fuel Composition
| Parameter | Value | Units | Factor | 15 | C
| Fuel Gas Molecular Weight (MWTave) | 2.0686 | g/mol | 0.087486 | kg/Sm3 |  | 177754.5 | [7 empty] | 24.5359
| Total Gas Mass HHV | 136.6584 | GJ/tonne | 11.9557 | MJ/Sm3
| Total Gas Mass LHV | 115.7304 | GJ/tonne | 10.1248 | MJ/Sm3
Step 2 | Calculated Properties from Gas Fuel Composition
2.1 To calculate stoichiometric waste gas flows
Stoichiometric waste gas (wet)
| Wsw = SUM Vp = | 2.8738 | m3/m3 gas burnt
Stoichiometric waste gas (dry)
| Wsd = SUM Vp -Vh2o = | 1.8763 | m3/m3 gas burnt
| 2.2 To calculate waste gas flows with excess air present |  |  |  | NB Excess air can be estimated from
[5 empty] | O2 measurements in dry flue gas: |  | O2 % = | 0.05 | % | Wsd=(21-%O2)/21*Wad
| Excess air |  | 0.18854 | % |  |  | Ea % = | 0.18854 | % | Wsd=(21-%O2)/21*(Wsd+Ea*Vs)
| Ea = | Va-Vs | 0.0018854 | [6 empty] | Wsd+Ea*Vs=Wsd*21/(21-%O2)
|  | Vs | [7 empty] | Ea*Vs=Wsd/(21-%O2)*[21-(21-%O2)]
| Va = actual air | [8 empty] | Ea*Vs=Wsd/(21-%O2)*%O2
| Vs = Stoichiometric air | 2.375 | m3/m3 gas burnt | [6 empty] | Ea=%O2/(21-%O2)*(Wsd/Vs)
Actual Air Va
| Va = Vs(1+Ea) | 2.3795 | m3/m3 gas burnt
Actual waste gas Wa:
| Waw (wet) =Wsw +Ea*Vs | 2.8782 | m3/m3 gas burnt |  |  |  | @ CO2 % | 0%
| Wad (dry) =Wsd +Ea*Vs | 1.8807 | m3/m3 gas burnt | @ O2 % | 0.05 | Measured O2 | @ CO2 % | 0%
0%
| Reported at reference O2%, dry | 2.189 | m3/m3 gas burnt | @ O2 % | 3 | Reference O2
2.3 To calculate waste gas flow rate based on natural gas consumption rate
| Assumed fuel usage (JMcW) | 56828.2781 | GJ/day | 55815.8644
|  | 2367.8449 | GJ/hr
| Calorific value | 0.010125 | GJ/m3
|  | 233865.3581 | Sm3 gas/hr | at | 15 | C
| Fuel flow | 221691.2114 | Nm3 gas/hr | at | 0 | C | Actual air flow | 527509.3435 | Nm3 air/hr
| Waste gas flow rate | Normal (Reference O2, dry, 0 C)
|  | 2.189 | m3/m3 gas burnt
|  | 485272.8247 | Nm3/hour | 51 | mg NOx / Nm3 | 6.8747 | g Nox / s
|  | 134.798 | Nm3/s | 100 | mg CO / Nm3 | 13.4798 | g CO / s
|  | Actual | (measured or calculated conditions)
|  | 2.8782 | m3/m3 gas burnt
| Temp (K) | 1273.15 | K |  | (temp | 1000 | oC)
|  | 2974075.7675 | m3/hour |  | (moisture | 34.6567 | %H2O) | to check
|  | 826.1322 | m3/s |  | (O2 | 0.05 | %O2)
fuel usuage for each boiler
|  | 0.65773 | gj/s | 55815.8644 | MW
|  | 39.4641 | gj/min
|  | 2367.8449 | gj/hr | 55815.8644 | MWh
|  | 56828.2781 | gj/day | 1339580.7458 | MWh/day
|  | 20742321.4928 | gj/year | 488946972.2034 | MWh/annum
Step 3 | Gas Flow Rate (to the Flare) |  |  |  |  | Volume to Mass conversion tool
| Parameter | Value | Units | Factor |  | Gas Volume | Units | Conversion Factor (mass/vol) | Gas Mass | Units
| Mass Flow Rate (M) | 20.46 | tonne/h | Em in 1 hour / Em |  | 0 | sm3 | 8.7486e-05 | 0 | tonne
| Mass Flow Rate (M) | 5.6833 | kg/s | - |  | 0 | nm3 | 9.229e-05 | 0 | tonne
| Mass Flow Rate (M) | 0.0056833 | tonne/s | - |  | 0 | scf | 2.4773e-06 | 0 | tonne
| Volumetric Flow Rate (V) | 198.2141 | mmscfd | 1 MMscf = 28.317 103m3 |  | 198.2141 | mmscf | 2.4773 | 491.04 | tonne
| Volume Flow Rate (V) @15 DegC | 233866.3731 | sm3/hr | -
| Volume Flow Rate (V) @15 DegC | 64.9629 | sm3/s | - |  | Ideal Gas Law Equations PV= nRT | Volume at 0 Deg C | Volume at 25 Deg C | Volume at 15 deg | Units
| Volume Flow Rate (V) @ 0 Deg C | 61.5812 | Nm3/s | Normalised to 0 Deg C |  | Volume (V) | 0.022414 | 0.024466 | 0.023645 | m3/mole
[6 empty] | Pressure (P) | 101325 | 101325 | 101325 | Pa (N/m2)
Step 4 | Efflux Volume Calculations |  |  |  |  | Number of Moles (n) | 1 | 1 | 1 | mole
| Parameter | Value | Units | Factor |  | Gas Constant (R) | 8.3145 | 8.3145 | 8.3145 | JK-1mol-1
| Flow Volume at STD conditions | 64.9629 | sm3/s | - |  | Temperature (T) | 273.15 | 298.15 | 288.15 | kelvins
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Temperature before combustion | 45 | Deg Celcius | -
| Stack Area (Prior to ambient mixing) | 0.63617 | m2 | -
| Efflux Velocity (Prior to Ignition) | 112.7467 | m/s | Vnozzle
| Temp of gas prior to release | 318.15 | Deg K | -
| Flow Volume at Stack (Actual Temp) | 71.7263 | m3/s | -
Step 5 | Heat Release Calculations
| Parameter | Value | Units | Factor
| Total Gas Mass LHV | 115.7304 | GJ/tonne | -
| Total Gas Mass LHV (Hc) | 115730445.7121 | J/kg | -
| Input Energy | 657.7347 | MW | -
| Combustion Efficiency (%) | 99%
| Total Heat Release (Qc or: Qtot) | 651157352.799 | Joule/s, W | Em*M
| Heat Release (H) | 155563417.4597 | cal/s | 1 J = 0.23890295762 Cal
| Radiative Loss Factor (f) | 25% | Left for heating | 75%
| Net Heat Release (Qn, ADMS5's Fb) | 488368014.5992 | J/s, W | Hr = (1-f)*H
| Net Heat Release Rate (Hr) | 116672563.0948 | cal/s | 1 J = 0.23890295762 Cal
| Stack Temperature Increase dTs | 2471.3408 | K | Assumed Cp = 1012 J/kg.K
| Air Temperature (T) | 288.15 | K | Ambeint air temperature
| Flow at Shrouded Flare (Actual Temp) | 1790.6091 | m3/s | -
| Efflux Velocity (Shrouded Flare) | 2814.6596 | m/s | -
| Momentum Flux (pi * Fm) | 7324.3479 | m4/s2 | elevated, without combustion air, assuming air temperature is 283K.
| Momentum Flux (pi * Fm) | 526279.3702 | m4/s2 | ground, with combustion air, assuming air temperature is 283K |  | https://files.ontario.ca/modelling-open-flares.pdf
Step 6 | Effective Stack Diameter (Pseudo Parameter)
| Parameter | Value | Units | Factor/Equation
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Stack Exit Temperature (Ts) | 1273 | K | US EPA Guidance
| Volume Flow Rate (V) @Stack Exit Temperature Deg 1000 Deg C | 287.1532 | m3/s | V @ 1000 Deg C = V @ 0 Deg C (Nm3)*(Ts/273)
| Exit Velocity (Vs) @ AERMOD DEFAULT VALUE | 20 | m/s | US EPA Guidance
| Exit Velocity (Vs) @ Stack T of 1000 Deg C | 451.3763 | m/s | Vs = V (m3/s) / (PI * D2/4)
| Effective diameter (ds) | 10.7535 | m | (ds) = (0.1066*[(Ts/(T*(Ts-T))*(Hr/Vs)]^0.5) = ds (ft) Iowa DNR
| Effective diameter (ds), AERSCREEN User’s Guide, USEPA | 10.6719 | m | (ds) = 9.88×10−4 × (HR × (1− f))^0.5 EPA
lb/MMBtu to g/GJ
| Effective Stack Height (Pseudo Parameter) | [5 empty] | lb to Kg | 0.45359
| Parameter | Value | Units | Factor/Equation |  |  | lb to g | 453.5924
| Stack height above ground (hs) | 65 | m | - |  |  | Btu to KJ | 1.0551
| Stack height above ground (hs) | 213.2546 | ft | 1 m = 3.280839895 ft |  |  | MMBtu to KJ | 1055056
| Effect flare release height (hsl) | 97.7045 | m | hsl (ft) = (hs + (7.54x10-3) * (Hr^0.478)) IOWA method | 0.0075455 |  | MMBtu to GJ | 1.0551
| Calculation check | 97.7285 | m | hsl (m) =hs +((0.00456)*((Hr/4.1868)^0.478)) IOWA method |  |  | lb/MMBtu to g/GJ | 429.9226
Step 7 | Emission Rates Calculations |  |  |  |  | US AP42 (lb/MMBtu)
| Parameter | Value | Units | Factor |  | Table 13.5-1 (English Units). NOx and Soot; Table 13.5-2 (English Units). CO | [6 empty] | Table 1.4-1
| NOx | 19.2287 | g/s | 0.0033833 |  | Component | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units
| CO | 87.6603 | g/s | 0.015424 |  | NOX | 29.2347 | g/GJ | 0.068 | lb/MMBtu | 0.0033833 | Mg/Mg | 0.18627 | lb/MMBtu | 190 | lb/MMSCF
| NMVOC | 55.1409 | g/s | 0.0097022 |  | Soot | 11.6079 | g/GJ | 0.027 | lb/MMBtu | 0.0013434 | Mg/Mg | 21.4929 | ug/L exhaust | 0.51 | kg soot/10^3 m3 fuel
| PM10 | 7.6349 | g/s | 0.0013434 |  | CO | 133.276 | g/GJ | 0.31 | lb/MMBtu | 0.015424 | Mg/Mg | 0.082353 | lb/MMBtu | 84 | lb/MMSCF
| S as H2S | 0 | g/s | 0 |  | https://www3.epa.gov/ttn/chief/ap42/ch13/final/C13S05_02-05-18.pdf
| H2S (5% unburnt) | 0 | g/s | 0
| SO2 (95% burnt S) | 0 | g/s | 0 |  | Acid gas flare Sox EF | [5 empty] | Mg/Mg
| BTEX by venting | 0 | g/s |  |  | Burn Pit Sox EF |  |  |  |  | 0 | Mg/Mg
| BTEX by flaring | 0 | g/s
| Summary Data |  |  | Summary Data
| Scenario | H2T |  | Scenario
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf |  | Data
| Emission Source | Flare Case2 |  | Emission Source
| Emission Source Height (m) | 65 |  | Emission Source Height (m)
| Equivalent Diameter of Area (m) | 0.9 |  | Equivalent Diameter of Area (m)
| Input Fuel Volume Flow Rate (mmscfd) | 198.2141 |  | Input Fuel Volume Flow Rate (mmscfd)
| Input Fuel Mass Flow Rate (t/h) | 20.46 |  | Input Fuel Mass Flow Rate (t/h)
| Input Energy (MWth) | 657.7347 |  | Input Energy (MWth)
| Op 1: Matching Heat and Momentum |  |  | Op 1: Matching Heat and Momentum
| Momentum Flux (ADMS5's Fm) (m4/s2) | 7324.3479 |  | Momentum Flux (ADMS5's Fm) (m4/s2)
| Heat Release (ADMS5's Fb) (MW) | 488.368 |  | Heat Release (ADMS5's Fb) (MW)
| Effective exit gas temperature (K) | 2759.4908 |  | Effective exit gas temperature (K)
| Effective exit velocity (m/s) | 45.9485 |  | Effective exit velocity (m/s)
| Effective exit diameter (m) | 1.6794 |  | Effective exit diameter (m)
| Op 2: Shrouded Flare or Point Source Approach |  |  | Op 2: Shrouded Flare or Point Source Approach
| Exit gas temperature (K) | 2759.4908 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 0.9 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 2814.6596 |  | Exit gas velocity (m/s)
| Op 3: USEPA Flare Approach |  |  | Op 3: USEPA Flare Approach
| Exit gas temperature (K) | 1273 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 10.6719 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 20 |  | Exit gas velocity (m/s)
| All: Emission Rate |  |  | All: Emission Rate
| NOx (g/s) | 19.2287 |  | NOx (g/s) | 4805.5556 | t/h | 17.3
| CO (g/s) | 87.6603 |  | CO (g/s) | 2125 | t/h | 7.65
| NMVOC (g/s) | 55.1409 |  | NMVOC (g/s) | 0 | t/h
| PM10 (g/s) | 7.6349 |  | PM10 (g/s) | 0
| H2S (g/s) | 0 |  | H2S (g/s) | 0
| SO2 (g/s) | 0 |  | SO2 (g/s) | 3369.4444 | t/h | 12.13
Note on E17: Chuansen Ren: This maximum rate is determined according to an academic paper: Bubbico R., Dusserre G., Mazzarotta B., 2016, Calculation of the flame size from burning liquid pools, Chemical Engineering Transactions, 53, 67-72 DOI: 10.3303/CET1653012
Note on F42: Chuansen Ren: Average Molecular Weight MWTave = ∑Wtr
Note on I105: C. Ren: at 15 Deg c
Note on I106: C. Ren: at 0 Deg C
Note on I107: 1 m3 = 35.3 scf
Note on I108: 1 m3 = 35.3 scf
Note on C131: Chuansen Ren: O. Reg. 419/05
Note on C154: Chuansen Ren: Use this in modelling
Note on C156: Chuansen Ren: Don't use this in modelling
Note on C157: Chuansen Ren: Don't use this in modelling either
Note on E161: Chuansen Ren: AP42
Note on E162: Chuansen Ren: AP42
Note on J162: Chuansen Ren: Grade B Factor developed using the higher (gross) heating value of the vent gas
Note on E163: Chuansen Ren: Assume X% overall combustion efficiency, but NMVOC has a lower efficiency than methane
Note on H163: Chuansen Ren: Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on J163: Chuansen Ren: Grade B Soot in concentration values: nonsmoking flares, 0 micrograms per liter (μg/L); lightly smoking flares, 40 μg/L; average smoking flares, 177 μg/L; and heavily smoking flares, 274 μg/L. Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on P163: Chuansen Ren: McEwen & Johnson (2012) https://doi.org/10.1080/10473289.2011.650040
Note on E164: Chuansen Ren: AP42, average smoking flares, g/m3
Note on J164: Chuansen Ren: Poorly

## Flare Calculations C3
| Scenario | H2T
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf
| Emission Source | Flare Case3
Inputs
Key Calculated Values
Stack Physical Parameters
| Parameter | Value | Units | Factor
Stack Name
Emission Points
Coordinates (X, Y)
| Release Height | 65 | m
| Diameter of Equivalent Area | 0.9 | m
| Fuel Flow Rate | 61.71 | tonne/hour | The maximum is determined by the formula as (0.081/1000)*(PI()*(C16/2)^2)*3600
Step 1 | Enter Gas Fuel Compostion
| Component | Formula | Molecular weight MWT | Component Mole Percentage Cmol | Relative Weight Wtr = Cmol/100*MWT | Component Weight Percentage Cwt = Wtr/MWTave | Gross Heating Value (Higher Heating Value) (GJ/t) | Net heating Value (Lower Heating Value) (GJ/t) | HHV*Cwt | LHV*Cwt | Fuel Molecular Carbon Content | Fuel Molecular Hydrogen Content | Component Carbon (Ratio to Fuel) | Component Hydrogen (Ratio to Fuel) | Comb. O2 required (Ratio to Fuel) | Comb. Air required (Ratio to Fuel) | Flue Molecular CO2 (Ration to Fuel) | Flue Molecular H2O (Ratio to Fuel) | LHV (J/g-mol)
| Nitrogen | N2 | 28 | 3.64 | 1.0192 | 5.88% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | #VALUE!
| Water | H2O | 18 | 0 | 0 | 0% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0 | #VALUE!
| Carbon Dioxide | CO2 | 44 | 0.77 | 0.3388 | 1.955% | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0077 | --- | #VALUE!
| Hydrogen Sulphide | H2S | 34 | 0 | 0 | 0% | 35.06 | 31.56 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1073040
| Methane | CH4 | 16 | 91.79 | 14.6864 | 84.73% | 55.5785 | 50.0368 | 47.0924 | 42.3969 | 1 | 4 | 0.9179 | 3.6716 | 1.8358 | 8.7419 | 0.9179 | 1.8358 | 800589.5357
| Ethane | C2H6 | 30 | 3 | 0.9 | 5.192% | 51.9418 | 47.5079 | 2.697 | 2.4668 | 2 | 6 | 0.06 | 0.18 | 0.105 | 0.5 | 0.06 | 0.09 | 1425235.8491
| Propane | C3H8 | 44 | 0.59 | 0.2596 | 1.498% | 50.37 | 46.3378 | 0.75441 | 0.69402 | 3 | 8 | 0.0177 | 0.0472 | 0.0295 | 0.14048 | 0.0177 | 0.0236 | 2038863.2708
| Butanes | C4H10, Isobutane, methylpropane | 58 | 0.09 | 0.0522 | 0.3012% | 49.4711 | 45.6469 | 0.14899 | 0.13747 | 4 | 10 | 0.0036 | 0.009 | 0.00585 | 0.027857 | 0.0036 | 0.0045 | 2647518.3076
|  | C4H10, n-Butane | 58 | 0.05 | 0.029 | 0.1673% | 49.4711 | 45.6469 | 0.082771 | 0.076373 | 4 | 10 | 0.002 | 0.005 | 0.00325 | 0.015476 | 0.002 | 0.0025 | 2647518.3076
| Pentanes | C5H12, Isopentane, methylbutane, 2-methylbutane | 72 | 0.04 | 0.0288 | 0.1662% | 48.9348 | 45.2638 | 0.081309 | 0.07521 | 5 | 12 | 0.002 | 0.0048 | 0.0032 | 0.015238 | 0.002 | 0.0024 | 3258997.0501
|  |  | 72 | 0 | 0 | 0% | 48.9348 | 45.2638 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3258997.0501
| Hexanes | C6H14 | 86 | 0.02 | 0.0172 | 0.09923% | 48.7106 | 45.1029 | 0.048337 | 0.044757 | 6 | 14 | 0.0012 | 0.0028 | 0.0019 | 0.0090476 | 0.0012 | 0.0014 | 3878847.7366
| Benzene | C6H6 | 78 | 0 | 0 | 0% | 42.2791 | 40.572 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3164618.6441
| Heptanes | C7H16 | 100 | 0 | 0 | 0% | 48.4733 | 44.9269 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 4492685.2289
| Toluene | C7H8 | 92 | 0 | 0 | 0% | 42.8689 | 40.9392 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 3766404.9269
| C8+ | C8H18 | 114 | 0 | 0 | 0% | 48.2902 | 44.7899 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5106048.4372
| Hydrogen | H2 | 2 | 0 | 0 | 0% | 141.7 | 120 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 240000
| Carbon Monoxide | CO | 28 | 0 | 0 | 0% | 10.16 | 10.16 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284480
| Ammonia | NH3 | 17 | 0.01 | 0.0017 | 0.009808% | 22.5 | 18.6 | 0.0022068 | 0.0018243 | 0 | 3 | 0 | 0.0003 | 7.5e-05 | 0.00035714 | 0 | 0.00015 | 316200
| Methanol | CH₃OH | 32 | 0 | 0 | 0% | 23 | 19.9 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 636800
| Insert components above this row | C6H14 | 86 |  | 0 | 0% |  |  | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total gas | --- | --- | 100 | 17.3329 | 100% | --- | --- | 50.9075 | 45.8934 | --- | --- | 1.0044 | 3.9207 | 1.9846 | 9.4504 | 1.0044 | 1.9604
| NMVOCs only | --- | --- | 3.8 | --- | 7.434% | --- | --- | --- | --- | --- | --- | --- | --- | ---
Note: If the analysis includes other compounds, add to species of closest molecular weight above.
Calculated Properties from Gas Fuel Composition
| Parameter | Value | Units | Factor | 15 | C
| Fuel Gas Molecular Weight (MWTave) | 17.3329 | g/mol | 0.73305 | kg/Sm3 |  | 590632.7756 | [7 empty] | 27.6759
| Total Gas Mass HHV | 50.9075 | GJ/tonne | 37.3178 | MJ/Sm3
| Total Gas Mass LHV | 45.8934 | GJ/tonne | 33.6422 | MJ/Sm3
Step 2 | Calculated Properties from Gas Fuel Composition
2.1 To calculate stoichiometric waste gas flows
Stoichiometric waste gas (wet)
| Wsw = SUM Vp = | 10.4305 | m3/m3 gas burnt
Stoichiometric waste gas (dry)
| Wsd = SUM Vp -Vh2o = | 8.4702 | m3/m3 gas burnt
| 2.2 To calculate waste gas flows with excess air present |  |  |  | NB Excess air can be estimated from
[5 empty] | O2 measurements in dry flue gas: |  | O2 % = | 0.05 | % | Wsd=(21-%O2)/21*Wad
| Excess air |  | 0.21391 | % |  |  | Ea % = | 0.21391 | % | Wsd=(21-%O2)/21*(Wsd+Ea*Vs)
| Ea = | Va-Vs | 0.0021391 | [6 empty] | Wsd+Ea*Vs=Wsd*21/(21-%O2)
|  | Vs | [7 empty] | Ea*Vs=Wsd/(21-%O2)*[21-(21-%O2)]
| Va = actual air | [8 empty] | Ea*Vs=Wsd/(21-%O2)*%O2
| Vs = Stoichiometric air | 9.4504 | m3/m3 gas burnt | [6 empty] | Ea=%O2/(21-%O2)*(Wsd/Vs)
Actual Air Va
| Va = Vs(1+Ea) | 9.4706 | m3/m3 gas burnt
Actual waste gas Wa:
| Waw (wet) =Wsw +Ea*Vs | 10.4507 | m3/m3 gas burnt |  |  |  | @ CO2 % | 9.684%
| Wad (dry) =Wsd +Ea*Vs | 8.4904 | m3/m3 gas burnt | @ O2 % | 0.05 | Measured O2 | @ CO2 % | 11.92%
11.83%
| Reported at reference O2%, dry | 9.8819 | m3/m3 gas burnt | @ O2 % | 3 | Reference O2
2.3 To calculate waste gas flow rate based on natural gas consumption rate
| Assumed fuel usage (JMcW) | 67969.9017 | GJ/day | 55815.8644
|  | 2832.0792 | GJ/hr
| Calorific value | 0.033642 | GJ/m3
|  | 84182.361 | Sm3 gas/hr | at | 15 | C
| Fuel flow | 79800.1454 | Nm3 gas/hr | at | 0 | C | Actual air flow | 755753.0524 | Nm3 air/hr
| Waste gas flow rate | Normal (Reference O2, dry, 0 C)
|  | 9.8819 | m3/m3 gas burnt
|  | 788575.3942 | Nm3/hour | 51 | mg NOx / Nm3 | 11.1715 | g Nox / s
|  | 219.0487 | Nm3/s | 100 | mg CO / Nm3 | 21.9049 | g CO / s
|  | Actual | (measured or calculated conditions)
|  | 10.4507 | m3/m3 gas burnt
| Temp (K) | 1273.15 | K |  | (temp | 1000 | oC)
|  | 3887133.0121 | m3/hour |  | (moisture | 18.758 | %H2O) | to check
|  | 1079.7592 | m3/s |  | (O2 | 0.05 | %O2)
fuel usuage for each boiler
|  | 0.78669 | gj/s | 55815.8644 | MW
|  | 47.2013 | gj/min
|  | 2832.0792 | gj/hr | 55815.8644 | MWh
|  | 67969.9017 | gj/day | 1339580.7458 | MWh/day
|  | 24809014.1316 | gj/year | 488946972.2034 | MWh/annum
Step 3 | Gas Flow Rate (to the Flare) |  |  |  |  | Volume to Mass conversion tool
| Parameter | Value | Units | Factor |  | Gas Volume | Units | Conversion Factor (mass/vol) | Gas Mass | Units
| Mass Flow Rate (M) | 61.71 | tonne/h | Em in 1 hour / Em |  | 0 | sm3 | 0.00073305 | 0 | tonne
| Mass Flow Rate (M) | 17.1417 | kg/s | - |  | 0 | nm3 | 0.0007733 | 0 | tonne
| Mass Flow Rate (M) | 0.017142 | tonne/s | - |  | 0 | scf | 2.0758e-05 | 0 | tonne
| Volumetric Flow Rate (V) | 71.3493 | mmscfd | 1 MMscf = 28.317 103m3 |  | 71.3493 | mmscf | 20.7576 | 1481.04 | tonne
| Volume Flow Rate (V) @15 DegC | 84182.7263 | sm3/hr | -
| Volume Flow Rate (V) @15 DegC | 23.3841 | sm3/s | - |  | Ideal Gas Law Equations PV= nRT | Volume at 0 Deg C | Volume at 25 Deg C | Volume at 15 deg | Units
| Volume Flow Rate (V) @ 0 Deg C | 22.1668 | Nm3/s | Normalised to 0 Deg C |  | Volume (V) | 0.022414 | 0.024466 | 0.023645 | m3/mole
[6 empty] | Pressure (P) | 101325 | 101325 | 101325 | Pa (N/m2)
Step 4 | Efflux Volume Calculations |  |  |  |  | Number of Moles (n) | 1 | 1 | 1 | mole
| Parameter | Value | Units | Factor |  | Gas Constant (R) | 8.3145 | 8.3145 | 8.3145 | JK-1mol-1
| Flow Volume at STD conditions | 23.3841 | sm3/s | - |  | Temperature (T) | 273.15 | 298.15 | 288.15 | kelvins
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Temperature before combustion | 38 | Deg Celcius | -
| Stack Area (Prior to ambient mixing) | 0.63617 | m2 | -
| Efflux Velocity (Prior to Ignition) | 39.6914 | m/s | Vnozzle
| Temp of gas prior to release | 311.15 | Deg K | -
| Flow Volume at Stack (Actual Temp) | 25.2506 | m3/s | -
Step 5 | Heat Release Calculations
| Parameter | Value | Units | Factor
| Total Gas Mass LHV | 45.8934 | GJ/tonne | -
| Total Gas Mass LHV (Hc) | 45893359.8892 | J/kg | -
| Input Energy | 786.6887 | MW | -
| Combustion Efficiency (%) | 99%
| Total Heat Release (Qc or: Qtot) | 778821790.6597 | Joule/s, W | Em*M
| Heat Release (H) | 186062829.2475 | cal/s | 1 J = 0.23890295762 Cal
| Radiative Loss Factor (f) | 25% | Left for heating | 75%
| Net Heat Release (Qn, ADMS5's Fb) | 584116342.9948 | J/s, W | Hr = (1-f)*H
| Net Heat Release Rate (Hr) | 139547121.9356 | cal/s | 1 J = 0.23890295762 Cal
| Stack Temperature Increase dTs | 1998.8706 | K | Assumed Cp = 1012 J/kg.K
| Air Temperature (T) | 288.15 | K | Ambeint air temperature
| Flow at Shrouded Flare (Actual Temp) | 1939.6317 | m3/s | -
| Efflux Velocity (Shrouded Flare) | 3048.9084 | m/s | -
| Momentum Flux (pi * Fm) | 928.148 | m4/s2 | elevated, without combustion air, assuming air temperature is 283K.
| Momentum Flux (pi * Fm) | 745095.9724 | m4/s2 | ground, with combustion air, assuming air temperature is 283K |  | https://files.ontario.ca/modelling-open-flares.pdf
Step 6 | Effective Stack Diameter (Pseudo Parameter)
| Parameter | Value | Units | Factor/Equation
| Stack Diameter (Prior to ambient mixing) (D) | 0.9 | m | -
| Stack Exit Temperature (Ts) | 1273 | K | US EPA Guidance
| Volume Flow Rate (V) @Stack Exit Temperature Deg 1000 Deg C | 103.3639 | m3/s | V @ 1000 Deg C = V @ 0 Deg C (Nm3)*(Ts/273)
| Exit Velocity (Vs) @ AERMOD DEFAULT VALUE | 20 | m/s | US EPA Guidance
| Exit Velocity (Vs) @ Stack T of 1000 Deg C | 162.4778 | m/s | Vs = V (m3/s) / (PI * D2/4)
| Effective diameter (ds) | 11.7605 | m | (ds) = (0.1066*[(Ts/(T*(Ts-T))*(Hr/Vs)]^0.5) = ds (ft) Iowa DNR
| Effective diameter (ds), AERSCREEN User’s Guide, USEPA | 11.6713 | m | (ds) = 9.88×10−4 × (HR × (1− f))^0.5 EPA
lb/MMBtu to g/GJ
| Effective Stack Height (Pseudo Parameter) | [5 empty] | lb to Kg | 0.45359
| Parameter | Value | Units | Factor/Equation |  |  | lb to g | 453.5924
| Stack height above ground (hs) | 65 | m | - |  |  | Btu to KJ | 1.0551
| Stack height above ground (hs) | 213.2546 | ft | 1 m = 3.280839895 ft |  |  | MMBtu to KJ | 1055056
| Effect flare release height (hsl) | 100.6265 | m | hsl (ft) = (hs + (7.54x10-3) * (Hr^0.478)) IOWA method | 0.0075455 |  | MMBtu to GJ | 1.0551
| Calculation check | 100.6527 | m | hsl (m) =hs +((0.00456)*((Hr/4.1868)^0.478)) IOWA method |  |  | lb/MMBtu to g/GJ | 429.9226
Step 7 | Emission Rates Calculations |  |  |  |  | US AP42 (lb/MMBtu)
| Parameter | Value | Units | Factor |  | Table 13.5-1 (English Units). NOx and Soot; Table 13.5-2 (English Units). CO | [6 empty] | Table 1.4-1
| NOx | 22.9986 | g/s | 0.0013417 |  | Component | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units | Emission Factor | units
| CO | 104.8467 | g/s | 0.0061165 |  | NOX | 29.2347 | g/GJ | 0.068 | lb/MMBtu | 0.0013417 | Mg/Mg | 0.18627 | lb/MMBtu | 190 | lb/MMSCF
| NMVOC | 12.7428 | g/s | 0.00074338 |  | Soot | 11.6079 | g/GJ | 0.027 | lb/MMBtu | 0.00053273 | Mg/Mg | 21.4929 | ug/L exhaust | 0.51 | kg soot/10^3 m3 fuel
| PM10 | 9.1318 | g/s | 0.00053273 |  | CO | 133.276 | g/GJ | 0.31 | lb/MMBtu | 0.0061165 | Mg/Mg | 0.082353 | lb/MMBtu | 84 | lb/MMSCF
| S as H2S | 0 | g/s | 0 |  | https://www3.epa.gov/ttn/chief/ap42/ch13/final/C13S05_02-05-18.pdf
| H2S (5% unburnt) | 0 | g/s | 0
| SO2 (95% burnt S) | 0 | g/s | 0 |  | Acid gas flare Sox EF | [5 empty] | Mg/Mg
| BTEX by venting | 0 | g/s |  |  | Burn Pit Sox EF |  |  |  |  | 0 | Mg/Mg
| BTEX by flaring | 0 | g/s
| Summary Data |  |  | Summary Data
| Scenario | H2T |  | Scenario
| Data | LP Flare Package BH001-PR-SPE-014-00009_B01.pdf |  | Data
| Emission Source | Flare Case3 |  | Emission Source
| Emission Source Height (m) | 65 |  | Emission Source Height (m)
| Equivalent Diameter of Area (m) | 0.9 |  | Equivalent Diameter of Area (m)
| Input Fuel Volume Flow Rate (mmscfd) | 71.3493 |  | Input Fuel Volume Flow Rate (mmscfd)
| Input Fuel Mass Flow Rate (t/h) | 61.71 |  | Input Fuel Mass Flow Rate (t/h)
| Input Energy (MWth) | 786.6887 |  | Input Energy (MWth)
| Op 1: Matching Heat and Momentum |  |  | Op 1: Matching Heat and Momentum
| Momentum Flux (ADMS5's Fm) (m4/s2) | 928.148 |  | Momentum Flux (ADMS5's Fm) (m4/s2)
| Heat Release (ADMS5's Fb) (MW) | 584.1163 |  | Heat Release (ADMS5's Fb) (MW)
| Effective exit gas temperature (K) | 2287.0206 |  | Effective exit gas temperature (K)
| Effective exit velocity (m/s) | 3.9375 |  | Effective exit velocity (m/s)
| Effective exit diameter (m) | 19.5124 |  | Effective exit diameter (m)
| Op 2: Shrouded Flare or Point Source Approach |  |  | Op 2: Shrouded Flare or Point Source Approach
| Exit gas temperature (K) | 2287.0206 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 0.9 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 3048.9084 |  | Exit gas velocity (m/s)
| Op 3: USEPA Flare Approach |  |  | Op 3: USEPA Flare Approach
| Exit gas temperature (K) | 1273 |  | Exit gas temperature (K)
| Stack Effective Diameter (m) | 11.6713 |  | Stack Effective Diameter (m)
| Exit gas velocity (m/s) | 20 |  | Exit gas velocity (m/s)
| All: Emission Rate |  |  | All: Emission Rate
| NOx (g/s) | 22.9986 |  | NOx (g/s) | 4805.5556 | t/h | 17.3
| CO (g/s) | 104.8467 |  | CO (g/s) | 2125 | t/h | 7.65
| NMVOC (g/s) | 12.7428 |  | NMVOC (g/s) | 0 | t/h
| PM10 (g/s) | 9.1318 |  | PM10 (g/s) | 0
| H2S (g/s) | 0 |  | H2S (g/s) | 0
| SO2 (g/s) | 0 |  | SO2 (g/s) | 3369.4444 | t/h | 12.13
Note on E17: Chuansen Ren: This maximum rate is determined according to an academic paper: Bubbico R., Dusserre G., Mazzarotta B., 2016, Calculation of the flame size from burning liquid pools, Chemical Engineering Transactions, 53, 67-72 DOI: 10.3303/CET1653012
Note on F42: Chuansen Ren: Average Molecular Weight MWTave = ∑Wtr
Note on I105: C. Ren: at 15 Deg c
Note on I106: C. Ren: at 0 Deg C
Note on I107: 1 m3 = 35.3 scf
Note on I108: 1 m3 = 35.3 scf
Note on C131: Chuansen Ren: O. Reg. 419/05
Note on C154: Chuansen Ren: Use this in modelling
Note on C156: Chuansen Ren: Don't use this in modelling
Note on C157: Chuansen Ren: Don't use this in modelling either
Note on E161: Chuansen Ren: AP42
Note on E162: Chuansen Ren: AP42
Note on J162: Chuansen Ren: Grade B Factor developed using the higher (gross) heating value of the vent gas
Note on E163: Chuansen Ren: Assume X% overall combustion efficiency, but NMVOC has a lower efficiency than methane
Note on H163: Chuansen Ren: Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on J163: Chuansen Ren: Grade B Soot in concentration values: nonsmoking flares, 0 micrograms per liter (μg/L); lightly smoking flares, 40 μg/L; average smoking flares, 177 μg/L; and heavily smoking flares, 274 μg/L. Emissions Estimation Protocol for Petroleum Refineries Version 3, Table 6-3
Note on P163: Chuansen Ren: McEwen & Johnson (2012) https://doi.org/10.1080/10473289.2011.650040
Note on E164: Chuansen Ren: AP42, average smoking flares, g/m3
Note on J164: Chuansen Ren: Poorly

## SSAir Quality - Emissions
Information Requirement | Fired Heater (6.9 MWth per unit) | Auxiliary boiler exhaust stack (35 MW thermal input) per unit | Auxiliary boiler exhaust stack (35 MW thermal input) per unit | Source
Operation Mode | Start up | Start up | Normal
Stack height (m) | TBC | TBC | TBC
Diameter (m) - sized to achieve 15 m/s on normal Op | 0.55 | 1.65 | 1.65 | Calculated
Stack location (X,Y) - Phase 1/2 | Phase 1 – 456247, 525229 Phase 2 – 456461, 525665 | 456314.65,525346.02 / 456349,525723 | 456314.65,525346.02 / 456349,525723
Fuel (if applicable) | Natural gas | Natural gas | Tail Gas (Hydrogen Rich)
Exhaust airflow at actual stack conditions (kg/s) at 40MW | 15.4583
Exhaust airflow at actual stack conditions (kg/s, rounded up) | 3 | 28.8767 | 24.0639 | BOL (highest)
Stack exhaust temperature (°C) | 200 | 259 | 155
Reference Oxygen Content (%) | 3 | 3 | 3
Reference Emission temperature (deg C) | 0 | 0 | 0
Reference H2O Content (%) | 0 | 0 | 0
Flue gas composition
Exhaust gas O2 vol% (wet) | 3.19 | 2.4968 | 1.57 | BOL
Exhaust gas O2 vol% (dry) |  |  |  | BOL
Exhaust gas CO2 mol% or vol% | 8.1 | 8.5342 | 2.27 | BOL
Exhaust gas H2O vol% | 16.62 | 16.4408 | 29.23 | BOL
Exhaust gas N2 vol% | 72.1 | 71.6778 | 65.98 | BOL
Exhaust gas Ar vol% | 0.77 | 0.8501 | 0.95 | BOL
Exhaust gas SO2 vol% | 0 | 0 | 0 | BOL
Other gas vol%
Raw/Actual exhaust flow (raw m3/s) | 4.1804 | 45.1462 | 32.9924 | Calculated
Normalised to T only exhaust flow (Nm³/s) | 2.4128 | 28.7965 | 21.0442 | Calculated
Reference exhaust flow (Nm³/s) | 1.9253 | 19.3657 | 15.5378 | Calculated
Velocity (m/s) | 17.5957 | 21.1137 | 15.4296 | PEIR (approximately)
Pollutants | 17.95
NOx emissions (mg/Nm3) Long Term | 225 | 18.81 | 78.99 | From PEIR, matches LCP ELV adjusted for Hydrogen Content
Nox emissions (mg/Nm3) Short Term
CO emissions (mg/Nm3) |  | 11.449
PM emissions (mg/Nm3) |  | 5 | 20 | From PEIR
Ammonia (mg/Nm3) |  | 6.96
SO2 | 3.9
NOx emissions (g/s) Long-term | 0.54288 | 0.54166 | 1.6623 | Calculated from above using Normalised to Temp flow
NOx emissions (g/s) Short-term
CO emissions (g/s) short-term |  | 0.32969
PM emissions (g/s) |  | 0.14398 | 0.42088 | Calculated from above using Normalised to Temp flow
Ammonia (g/s) |  | 0.20042
SO2 (g/s) | 0.00941 | 0