## W2 Wastewater Concentrations
|  | Flow | 120 | m3/h |  | Flow | 23.4 | m3/h |  | Flow | 143.4 | m3/h
|  | Cooling tower blowdown |  |  |  | RO Reject |  |  |  | Combined Reject for Assessment
|  | Concentration |  | Flux |  | Concentration |  | Flux |  | Concentration |  | Flux
Total Organic Carbon | TOC | mg/l | 50 | g/h | 6000 | mg/l | 0 | g/h | 0 | mg/l | 41.841 | g/h | 6000
Chemical Oxygen Demand | COD | mg/l | 150 | g/h | 18000 | mg/l | 0 | g/h | 0 | mg/l | 125.523 | g/h | 18000
Total Suspended Solids | TSS | mg/l | 30 | g/h | 3600 | mg/l | 10 | g/h | 234 | mg/l | 26.7364 | g/h | 3834
Calcium | Ca(2+) | mg/l | 252.6104 | g/h | 30313.253 | mg/l | 371 | g/h | 8681.4 | mg/l | 271.9292 | g/h | 38994.653
Magnesium | Mg(2+) | mg/l | 58.2524 | g/h | 6990.2913 | mg/l | 96 | g/h | 2246.4 | mg/l | 64.4121 | g/h | 9236.6913
Iron (total) | Fe (total) | mg/l | 2.75 | g/h | 330 | mg/l | 0 | g/h | 0 | mg/l | 2.3013 | g/h | 330
Manganese | Mn | mg/l | 0.3 | g/h | 36 | mg/l | 0 | g/h | 0 | mg/l | 0.25105 | g/h | 36
Chloride | Cl(-) | mg/l | 221 | g/h | 26520 | mg/l | 372 | g/h | 8704.8 | mg/l | 245.6402 | g/h | 35224.8
Sulfate | SO4(2-) | mg/l | 493 | g/h | 59160 | mg/l | 769 | g/h | 17994.6 | mg/l | 538.0377 | g/h | 77154.6
Ammonia | N-NH4(+) | mg/l | 7 | g/h | 840 | mg/l | 0 | g/h | 0 | mg/l | 5.8577 | g/h | 840
Sodium | Na(+) | mg/l | 131 | g/h | 15720 | mg/l | 156 | g/h | 3650.4 | mg/l | 135.0795 | g/h | 19370.4
Fluoride | F(-) | mg/l | 1.4 | g/h | 168 | mg/l | 2 | g/h | 46.8 | mg/l | 1.4979 | g/h | 214.8
Sulphide, easily released | S(2-) | mg/l | - | g/h | - | mg/l | - | g/h | - | mg/l | - | g/h | -
Sulphite | SO3(2-) | mg/l | - | g/h | - | mg/l | - | g/h | - | mg/l | - | g/h | -
Arsenic | As | µg/l | - | g/h | - | µg/l | - | g/h | - | µg/l | - | g/h | -
Cadmium | Cd | µg/l | 0.34 | g/h | 0.0408 | µg/l | - | g/h | - | µg/l | 0.28452 | g/h | 0.0408
Chromium | Cr | µg/l | 7.7 | g/h | 0.924 | µg/l | - | g/h | - | µg/l | 6.4435 | g/h | 0.924
Copper | Cu | µg/l | 12.1 | g/h | 1.452 | µg/l | - | g/h | - | µg/l | 10.1255 | g/h | 1.452
Nickel (Ni) | Ni | µg/l | 8.8 | g/h | 1.056 | µg/l | - | g/h | - | µg/l | 7.364 | g/h | 1.056
Lead (Pb) | Pb | µg/l | 100 | g/h | 12 | µg/l | - | g/h | - | µg/l | 83.682 | g/h | 12
Zinc (Zn) | Zn | µg/l | 200 | g/h | 24000 | mg/l | - | g/h | - | mg/l | 167.364 | g/h | 24000
Mercury (Hg) | Hg | µg/l | - | g/h | - | µg/l | - | g/h | - | µg/l | - | g/h | -
Total nitrogen (as N) | N (total) | mg/l | 27 | g/h | 3240 | mg/l | 24.975 | g/h | 584.415 | mg/l | 26.6696 | g/h | 3824.415
Total phosphorus (as P) | P (total) | mg/l | 4.6 | g/h | 552 | mg/l | - | g/h | - | mg/l | 3.8494 | g/h | 552
Key:
Parameters included in the existing Permit
Parameters assessed at current permit limits as a worst case
Parameters that BATc footnotes say aren't relevant
Parameters that BATc footnotes say are either/ or

## Test 1_Coastal
Test 1 - Coastal
[7 empty] | Refer to: |  | https://www.gov.uk/guidance/surface-water-pollution-risk-assessment-for-your-environmental-permit
Take values from previous table and simply compare with the EQS. Distinguish between the avg and max values.
Any value above the EQS fails the test and must be considered for Test 2.
Any value below the EQS passes and can be screened out
Some abbreviations are used in this table, O is operational, SP is specific pollutant, PHS is priority hazardous substance, PS is priority substance, OP is other pollutant, PAH is polyaromatic hydrocarbons.
Element |  | Unit | Concentration | Annual average EQS (micrograms per litre) | Pemit Limits (EA) (mg/l) | Annual average EQS (mg/l) | Maximum allowable concentration EQS (micrograms per litre) | Maximum allowable concentration EQS (mg/l) | Category | Similar chemical | Screening Test 1 (Permit Limits) | Screening Test 1 (AA) | Screening Test 1 (MAC)
Total Organic Carbon | TOC | mg/l | 41.841 |  | 50 | [5 empty] | Pass
Chemical Oxygen Demand | COD | mg/l | 125.523 |  | 150 | [5 empty] | Pass
Total Suspended Solids | TSS | mg/l | 26.7364 | 100000 | 30 | 100 | - |  |  | - | Pass | Pass |  | Refer to: https://www.gov.uk/government/publications/water-companies-water-treatment-works-discharge-limits-for-environmental-permits/water-companies-water-treatment-works-discharge-limits-for-environmental-permits#:~:text=95-percentile%20EQS%20.-,Suspended%20solids%20discharge%20limits%20to%20surface%20water,solids%20limit%20for%20a%20discharge.
Calcium | Ca(2+) | mg/l | 271.9292
Magnesium | Mg(2+) | mg/l | 64.4121
Iron (total) | Fe (total) | mg/l | 2.3013 | 1000 |  | 1 | Not applicable | Not applicable | SP | Iron - dissolved |  | Fail
Manganese | Mn | mg/l | 0.25105 | Not applicable |  | Not applicable | Not applicable | Not applicable | SP | -
Chloride | Cl(-) | mg/l | 245.6402 | Not applicable |  | Not applicable | Not applicable | Not applicable | O | -
Sulfate | SO4(2-) | mg/l | 538.0377 | Not applicable |  | Not applicable | Not applicable | Not applicable | O | -
Ammonia | N-NH4(+) | mg/l | 5.8577 | 21 |  | 0.021 | Not applicable | Not applicable | SP | Ammonia - un-ionised |  | Fail |  | https://www.irishstatutebook.ie/eli/2009/si/272/made/en/pdf
Sodium | Na(+) | mg/l | 135.0795
Fluoride | F(-) | mg/l | 1.4979 | 5000 | 25 | 5 | 15000 | 15 | O | Fluoride - dissolved | Pass | Pass | Pass
Sulphide, easily released | S(2-) | mg/l | - | Not applicable | 0.2 | Not applicable | 10 | 0.01 | O | Hydrogen sulphide | - | - | -
Sulphite | SO3(2-) | mg/l | - | Not applicable | 20 | Not applicable | Not applicable | Not applicable | O | - | - | - | -
Arsenic | As | mg/l | - | 25 | 0.05 | 0.025 | Not applicable | Not applicable | SP | - | - | - | -
Cadmium | Cd | mg/l | 0.00028452 | 0.2 | 0.005 | 0.0002 | Not applicable | Not applicable | PHS | Cadmium and its compounds (dissolved) | Pass | Fail
Chromium | Cr | mg/l | 0.0064435 | Not applicable | 0.05 | 0.0006 | 32 (95th percentile) | 0.032 (95th percentile) | SP | Chromium (VI) - dissolved | Pass | Fail | Pass
Copper | Cu | mg/l | 0.010126 | 3.76 | 0.05 | 0.00376 | Not applicable | Not applicable | SP | Copper - dissolved (Dissolved organic carbon (DOC) less than or equal to 1 milligram per litre (mg/l)) | Pass | Fail
|  |  | - | 3.76 + (2.677 x ((DOC/2) –0.5)) μg/l | - | (3.76 + (2.677 x ((DOC/2) –0.5)))/1000 | Not applicable | Not applicable | SP | Copper - dissolved (Dissolved organic carbon (DOC) greater than 1mg/l) | - | - | -
Nickel (Ni) | Ni | mg/l | 0.007364 | 8.6 | 0.05 | 0.0086 | 34 | 0.034 | PS | - | Pass | Pass | Pass
Lead (Pb) | Pb | mg/l | 0.083682 | 1.3 | 0.02 | 0.0013 | 14 | 0.014 | PS | Lead and its compounds (dissolved) | Fail | Fail | Fail
Zinc (Zn) | Zn | mg/l | 0.16736 | 6.8 | 0.2 | 0.0068 | Not applicable | Not applicable | SP | Zinc - dissolved plus ambient background concentration. For saltwater, an Ambient Background Concentration of 1.1 µg/l is recommended. | Fail | Fail
Mercury (Hg) | Hg | mg/l | - | Not applicable | 0.003 | Not applicable | 0.07 | 7e-05 | PHS | - | - | - | -
Total nitrogen (as N) | N (total) | mg/l | 0.02667 | 0.567
Total phosphorus (as P) | P (total) | mg/l | 0.0038494
Note on L21: Livia Machado De Almeida: Permit Limits that allowed 3 new passes
Note on B30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Seems like this is ionized ammonia
Note on M37: Livia Machado De Almeida: New fail, we didn't realized the concentration failed the AA EQS before

## Test 2_Coastal
We are not discharging to a low flow channel
This test is n/a
Therefore go to test 3

## Test 3_Coastal
Note: It is not a location with restricted dilution
Go to test 4

## Test 4_Coastal
Do these apply to our site?
No
No
Ok - go to test 5

## Test 5_Coastal
|  |  | 143.4 | m3/hr
|  |  | 0.039833 | m3/s
| Step 1 |  |  | Step 2 | [7 empty] | Step 3
Parameter | Release Con (mg/l) | Release Con (µg/l) | Flux (mg/s) | Avg Bac Con (mg/l) | PL Conc (mg/l) | EQS AA (mg/l) | EQS AA (µg/l) | EQS MAC (mg/l) | Capacity - PL (mg/l) | Capacity - AA (mg/l) | Capacity - MAC (mg/l) | Eff Vol Flux Per Lim (l/s) | Eff Vol Flux AA (l/s) | Eff Vol Flux MAC (l/s) | Max Allow Vol Flux (l/s)
Iron (total) | 2.3013 | 2301.2552 | 91.6667 | 0.238 | - | 1 | 1000 | - | - | 0.762 | - | - | 120.2975 | - | 3500
Cadmium | 0.00028452 | 0.28452 | 0.011333 | 6.7e-05 | 0.005 | 0.0002 | 0.2 | - | 0.004933 | 0.000133 | - | 2.2975 | 85.213 | - | 3500
Chromium | 0.0064435 | 6.4435 | 0.25667 | 0.00522 | 0.05 | 0.006 |  | 0.032 | 0.04478 | 0.00078 | - | 5.7317 | 329.0598 | - | 3500
Copper | 0.010126 | 10.1255 | 0.40333 | 0.00063 | 0.05 | 0.00376 | 3.76 | - | 0.04937 | 0.00313 | - | 8.1696 | 128.8605 | - | 3500
Lead (Pb) | 0.083682 | 83.682 | 3.3333 | 0.000128 | 0.02 | 0.0013 | 1.3 | 0.014 | 0.019872 | 0.001172 | 0.013872 | 167.7402 | 2844.1411 | 240.2922 | 3500
Zinc (Zn) | 0.16736 | 167.364 | 6.6667 | 0.002167 | 0.2 | 0.0068 | 6.8 | - | 0.19783 | 0.004633 | - | 33.6985 | 1438.9524 | - | 3500
Ammonia | 5.8577 | 5857.7406 | 233.3333 | 0.00027 | - | 0.6 | 600 | - | - | 0.59973 | - | - | 389.064 | - | 3500
Ammonia
INPUT Parameter: |  | N-NH4(+) | Ammonium expressed as nitrogen (N-NH₄⁺)
AA EQS for Ammonium (N-NH₄⁺) in the UK for Estuarine and Coastal Waters
Reference: | UK Technical Advisory Group (UKTAG) report on Environmental Standards (Phase 1, 2008)
sets the annual average EQS for ammonium (expressed as nitrogen, N-NH₄⁺) in estuarine and coastal waters at 0.6 mg/L
https://arup-my.sharepoint.com/:b:/p/kevin_barry/EY87ZNTbbpNHhY4f3bY20vMBQJsso8uhuYdHJYA3qe6H7Q?xsdata=MDV8MDJ8TGl2aWEuTWFjaGFkb0RlQWxtZWlkYUBhcnVwLmNvbXxkYWMxOWI1ZDczNGM0ZjgyMWY3NjA4ZGUxMTNjMGVmY3w0YWU0OGI0MTAxMzc0NTk5ODY2MWZjNjQxZmU3N2JlYXwwfDB8NjM4OTY3MTQ2ODA2MzMzMTQ1fFVua25vd258VFdGcGJHWnNiM2Q4ZXlKRmJYQjBlVTFoY0draU9uUnlkV1VzSWxZaU9pSXdMakF1TURBd01DSXNJbEFpT2lKWGFXNHpNaUlzSWtGT0lqb2lUV0ZwYkNJc0lsZFVJam95ZlE9PXwwfHx8&sdata=dTJxYitpVXFwZ2xOYWZZUGNUWGNoVGpaZFo2OG12T2xVbVdGWC9vODBVYz0%3d
Note on G26: Livia Machado De Almeida: Collumns G,K and N added to account for the Permit Limits