## DV Freq Export
|  |  | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave | 1/3 Octave
Filename | Elapsed time |  | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | 1/3 Oct Leq (SR) [dB] | Events
| [hh:mm:ss] | Date & time | 25 Hz | 31.5 Hz | 40 Hz | 50 Hz | 63 Hz | 80 Hz | 100 Hz | 125 Hz | 160 Hz | 200 Hz | 250 Hz | 315 Hz | 400 Hz | 500 Hz | 630 Hz | 800 Hz | 1000 Hz | 1250 Hz | 1600 Hz | 2000 Hz | 2500 Hz | 3150 Hz | 4000 Hz | 5000 Hz | 6300 Hz | 8000 Hz | 10000 Hz | Total A
619 | 0:00 | 46107.4102 | 59.6 | 55.8 | 60.7 | 76.1 | 58.8 | 58.8 | 56.8 | 55.8 | 56.5 | 55.7 | 56.1 | 52.7 | 51.9 | 53.9 | 55 | 55.1 | 55.1 | 51.9 | 52.2 | 49.3 | 55.5 | 46.8 | 44.6 | 45.3 | 38.2 | 35 | 31.8 | 63.5 | 1
620 | 0:01 | 46107.411 | 58.9 | 63 | 61.5 | 75.3 | 63.9 | 67.3 | 68.6 | 65.7 | 69 | 71.3 | 73.1 | 71.1 | 71.3 | 70.7 | 69.2 | 68.4 | 68.7 | 67 | 68.4 | 69 | 66 | 64 | 64.2 | 62.5 | 60.5 | 58.2 | 55.9 | 78.7 | 1
621 | 0:01 | 46107.4119 | 60.5 | 61.2 | 62.7 | 63.6 | 60.7 | 64.1 | 70.2 | 63.4 | 68.8 | 64.9 | 65.1 | 68.9 | 66.5 | 65.2 | 62.6 | 62.8 | 63.9 | 60.5 | 62.1 | 62.1 | 59.7 | 58.7 | 58 | 56.1 | 55.2 | 49.6 | 46.3 | 73 | 1
622 | 0:01 | 46107.4128 | 68.4 | 66.8 | 69.7 | 78 | 70.4 | 67.7 | 68.3 | 65.5 | 68.2 | 67.4 | 66.7 | 71.2 | 69.5 | 67.7 | 65.3 | 63.7 | 63.4 | 63 | 63.2 | 64.4 | 61.1 | 59.3 | 58.4 | 57.8 | 56.8 | 52.8 | 49.9 | 74.7 | 1
623 | 0:01 | 46107.4151 | 76.6 | 76.7 | 76.6 | 91 | 74.3 | 76 | 83.5 | 78.5 | 83.2 | 96.9 | 85.5 | 88.1 | 87.9 | 88.1 | 82.4 | 84.2 | 81.9 | 86.9 | 84.5 | 82.9 | 82.9 | 81.8 | 79.3 | 77.3 | 76.4 | 75.2 | 74.4 | 95.3 | 1
624 | 0:01 | 46107.4159 | 79.2 | 78.9 | 83.9 | 101.8 | 87.7 | 81.7 | 96 | 83 | 88.2 | 92 | 83.2 | 86 | 87.7 | 89.1 | 86.4 | 87.1 | 86.1 | 86 | 85.5 | 83.4 | 84.6 | 85.3 | 81.5 | 79.5 | 80.5 | 81.6 | 78.4 | 96.6 | 1
625 | 0:01 | 46107.4168 | 71.6 | 69.3 | 71.2 | 79.9 | 72.2 | 71.2 | 83.4 | 71.9 | 72 | 77.2 | 75.6 | 85.5 | 85.9 | 86.2 | 81.7 | 79.7 | 78.8 | 80.5 | 79.6 | 77.6 | 77.5 | 76.9 | 73.7 | 72.5 | 72.5 | 70.4 | 68.8 | 90.7 | 1
626 | 0:01 | 46107.4194 | 83.2 | 80.4 | 86.6 | 96.5 | 82.6 | 81.1 | 82.5 | 84.1 | 94.9 | 84.8 | 84.2 | 87.1 | 86.8 | 84.3 | 79.9 | 76.2 | 76.3 | 75.6 | 72.3 | 69.7 | 67.1 | 64.5 | 62.9 | 62.5 | 62 | 59.9 | 55.9 | 89 | 1
627 | 0:01 | 46107.4205 | 82.3 | 82.5 | 84.3 | 99.9 | 83 | 83.2 | 89.6 | 87.9 | 91.6 | 86.6 | 84.4 | 83.6 | 83.3 | 80.5 | 78.3 | 73.8 | 72.9 | 72.5 | 71 | 69.9 | 68.2 | 66.1 | 65 | 62.5 | 61.1 | 60.8 | 58.6 | 86.9 | 1
628 | 0:01 | 46107.4217 | 81.7 | 76.8 | 84.6 | 93.4 | 89.6 | 86.2 | 84.6 | 85 | 94.5 | 84.2 | 79 | 71 | 71.7 | 70.9 | 69.8 | 68.4 | 64.6 | 66.4 | 60.4 | 58.5 | 58.5 | 58.2 | 55 | 53.3 | 51.9 | 50.3 | 47.8 | 83.1 | 1
629 | 0:01 | 46107.4261 | 53 | 50.4 | 51 | 53.9 | 50.6 | 47.4 | 65 | 49.3 | 51.9 | 63.5 | 59.5 | 59.5 | 57.9 | 56.8 | 58.6 | 56.1 | 53.8 | 46.9 | 41.8 | 40.4 | 39.6 | 38.3 | 36.8 | 35 | 34.7 | 35.5 | 34.3 | 63.2 | 1
630 | 0:01 | 46107.4279 | 55.3 | 58.5 | 57.5 | 59.7 | 56.3 | 54.5 | 58.6 | 53.8 | 52.4 | 61.1 | 54.8 | 54.7 | 55.9 | 55.8 | 56.5 | 54.6 | 52.5 | 48.7 | 46.1 | 43.7 | 42.6 | 42.3 | 43.3 | 41.3 | 35.9 | 33.6 | 30.3 | 61.7 | 1
631 | 0:01 | 46107.4314 | 56.5 | 53.9 | 48.4 | 48.8 | 45.8 | 45.4 | 46.6 | 46.1 | 45.1 | 45.5 | 48.3 | 47.8 | 47.3 | 51 | 47.3 | 44.2 | 43.2 | 44.4 | 45.7 | 46.4 | 47.5 | 44.2 | 42.3 | 39.9 | 35.8 | 33.4 | 30.8 | 56.6 | 1
632 | 0:01 | 46107.4327 | 55.7 | 53.4 | 52 | 54.1 | 50.1 | 49.7 | 48.7 | 47.4 | 48.1 | 49.2 | 46.7 | 44.1 | 44.8 | 46.3 | 45.2 | 45.4 | 46.3 | 45.5 | 45.9 | 48.4 | 46.3 | 47.9 | 42.5 | 41.5 | 38.8 | 38.5 | 36.7 | 57.1 | 1
633 | 0:01 | 46107.4362 | 53.6 | 53.6 | 53.7 | 53.1 | 54.1 | 51.1 | 51.4 | 51.8 | 46.9 | 45.9 | 56.3 | 52.1 | 49.7 | 46.1 | 47.1 | 41 | 39.9 | 41.6 | 39.5 | 43.2 | 38.3 | 37.5 | 36.4 | 33.5 | 31.6 | 28.2 | 26.1 | 54.6 | 1
634 | 0:01 | 46107.4384 | 54 | 52 | 54.1 | 52.6 | 52.6 | 51.7 | 49.3 | 51.9 | 50.3 | 48 | 48.7 | 45.4 | 43 | 43.7 | 42.7 | 45.1 | 46.5 | 45.4 | 43.7 | 41 | 38.5 | 35.9 | 34.7 | 34 | 30.9 | 27 | 26.3 | 53.8 | 1
635 | 0:01 | 46107.4494 | 60.6 | 57.3 | 58.1 | 57.7 | 54.7 | 47.5 | 50 | 51.9 | 58.3 | 77.1 | 59.5 | 55 | 54.7 | 58.2 | 58.9 | 54.6 | 53.5 | 51.2 | 50 | 49.6 | 50.9 | 49.5 | 53.1 | 49.3 | 51.1 | 58.3 | 47 | 68.5 | 1
636 | 0:00 | 46107.4494 | 55.8 | 55.1 | 50 | 55.7 | 54 | 46.6 | 48.3 | 47.7 | 59.1 | 78.6 | 56.7 | 53.7 | 52.3 | 54.4 | 54.3 | 54 | 53.5 | 48.2 | 46.9 | 46.9 | 48.8 | 48.3 | 51.8 | 47.5 | 48.7 | 53.8 | 42.7 | 68.4 | 0
637 | 0:01 | 46107.4501 | 54 | 53.3 | 49.9 | 54.2 | 48.7 | 48.7 | 51.1 | 53.7 | 53.3 | 52.9 | 59.6 | 60.5 | 60 | 63.2 | 63.6 | 61.2 | 55.4 | 56.6 | 55.6 | 54.9 | 54.8 | 53.2 | 53.2 | 49.4 | 47.8 | 47.3 | 42.7 | 68.5 | 1
638 | 0:01 | 46107.459 | 60.7 | 58.8 | 56.6 | 56.8 | 54 | 55.2 | 64.2 | 63.5 | 61.9 | 60.7 | 58.9 | 58.5 | 59 | 58.7 | 60.1 | 56.5 | 56.9 | 54.5 | 54.4 | 49.2 | 45.3 | 41.8 | 40.2 | 39.2 | 36.1 | 33.1 | 31.1 | 65.4 | 1
639 | 0:01 | 46107.4601 | 61.9 | 58.5 | 57 | 56.9 | 55 | 57.6 | 67.6 | 67.8 | 65.8 | 64.4 | 63.1 | 61 | 60.8 | 62.1 | 62.6 | 61.9 | 57.4 | 56.2 | 54.2 | 55.9 | 53 | 49.1 | 46.8 | 44 | 40.6 | 37.6 | 35.2 | 68.4 | 1
640 | 0:01 | 46107.4692 | 55 | 55.8 | 43.6 | 45.2 | 46.2 | 50.5 | 44.3 | 44.5 | 43.8 | 45.3 | 43.3 | 43.2 | 45.8 | 56 | 46 | 46.5 | 47.5 | 45.3 | 47.8 | 47.6 | 47.1 | 46.4 | 41.8 | 40.3 | 34.4 | 31.6 | 28.6 | 58.3 | 1
641 | 0:01 | 46107.5331 | 64.9 | 63.5 | 72.1 | 56.6 | 52.2 | 52.8 | 50.7 | 50.3 | 52.4 | 52 | 50.2 | 51.6 | 49.9 | 50 | 49.1 | 48.1 | 47.3 | 46.2 | 44.9 | 43.5 | 40.6 | 37.5 | 33.4 | 31.5 | 29.3 | 26.2 | 23.3 | 56.5 | 1
642 | 0:01 | 46107.5341 | 68.1 | 65.7 | 71.4 | 60.7 | 56.9 | 56.7 | 51 | 49.6 | 46.7 | 48.8 | 46.5 | 46.9 | 46.4 | 43.7 | 44 | 44.6 | 45.1 | 42.3 | 40.9 | 39 | 36.3 | 36.9 | 33.3 | 29.1 | 26.6 | 22.7 | 20.3 | 52.9 | 1
643 | 0:01 | 46107.5351 | 61.8 | 59.7 | 68.5 | 53.1 | 49.1 | 55.5 | 51.2 | 49.5 | 51.1 | 48.8 | 46 | 47.4 | 44.9 | 45.4 | 47.1 | 47.6 | 49.3 | 46.1 | 45.3 | 43.7 | 39.2 | 38.6 | 35.2 | 33 | 31.6 | 28.9 | 26.3 | 55.7 | 1
644 | 0:01 | 46107.5444 | 58.3 | 57.9 | 54.6 | 54.1 | 56.9 | 62.1 | 50.9 | 52 | 61.8 | 65.1 | 50.7 | 51.2 | 52.9 | 58.2 | 54.7 | 55.8 | 56.3 | 54.4 | 53.8 | 53.7 | 51.9 | 51.2 | 48.7 | 41.8 | 37.4 | 34.1 | 29.6 | 64.8 | 1
645 | 0:01 | 46107.5533 | 64.6 | 62.4 | 54.5 | 58.6 | 56.4 | 55.2 | 53 | 50.5 | 46.5 | 46.5 | 47.3 | 46.1 | 49.8 | 45.6 | 43.8 | 44.3 | 42.2 | 43.8 | 40.6 | 37.9 | 37.1 | 36.6 | 32.2 | 29.9 | 29 | 24.3 | 21.1 | 52.9 | 1
646 | 0:01 | 46107.5823 | 68.6 | 64.6 | 63.5 | 62 | 57.2 | 54 | 54.1 | 51.3 | 51.8 | 48.5 | 45 | 48.4 | 46.4 | 43.7 | 42.9 | 45.2 | 44.7 | 43.7 | 45.1 | 41.3 | 40.7 | 40.7 | 40.2 | 38.8 | 38.1 | 39.6 | 34 | 54.6 | 1
647 | 0:01 | 46107.5838 | 67 | 63.2 | 63.5 | 57.8 | 56.8 | 57.6 | 52.1 | 50.5 | 52.7 | 48.6 | 45.7 | 45.4 | 44.9 | 44.2 | 43.7 | 46.7 | 46.7 | 43.1 | 42.5 | 39.4 | 38.2 | 37.9 | 37.7 | 35.9 | 34.6 | 34.6 | 34.7 | 54 | 1
648 | 0:01 | 46107.5852 | 70.9 | 68.6 | 65.6 | 62.6 | 59.1 | 56.4 | 54.4 | 52.1 | 56.5 | 56.1 | 46.9 | 50.4 | 49.7 | 47.2 | 49.1 | 52.6 | 49.1 | 49.1 | 48.8 | 47.7 | 48.1 | 46.3 | 44.3 | 45 | 42.8 | 41.4 | 37.4 | 59.7 | 1
649 | 0:01 | 46107.5863 | 66.1 | 63 | 60.2 | 57.4 | 55.1 | 53.5 | 51.8 | 49.8 | 53.4 | 51.2 | 46.5 | 49.3 | 46.3 | 45.6 | 45.5 | 50.8 | 47.7 | 48.2 | 46.2 | 44.4 | 45.8 | 44.5 | 41.5 | 41.4 | 41.1 | 40.6 | 35.6 | 57.5 | 1
650 | 0:01 | 46107.5871 | 73.3 | 71.4 | 68.6 | 66.3 | 62.2 | 59.3 | 56.5 | 56.2 | 59.5 | 59.7 | 50.7 | 51.6 | 53.5 | 51.4 | 51.6 | 57 | 53.6 | 53.1 | 52.5 | 50 | 49.8 | 48.4 | 44.3 | 42.9 | 40.8 | 40.5 | 37 | 62.8 | 1
651 | 0:01 | 46107.5926 | 56.1 | 55.5 | 54.6 | 54.6 | 53.7 | 51.9 | 51 | 49.3 | 49.5 | 49.2 | 48 | 45.9 | 47.6 | 49.1 | 49 | 48.3 | 50.4 | 45.4 | 45.5 | 45.8 | 44.8 | 43.1 | 41.9 | 41 | 37.9 | 36.2 | 34.7 | 57.3 | 1
652 | 0:01 | 46107.5936 | 63 | 61.1 | 58.1 | 55.8 | 54.8 | 51.9 | 50.7 | 48.6 | 48.2 | 51.9 | 50.2 | 46.5 | 51.3 | 50.4 | 47.4 | 44 | 44.4 | 42.4 | 40.7 | 41.1 | 41.8 | 41.3 | 39.4 | 39.3 | 37.6 | 35.3 | 36.2 | 55.3 | 1
653 | 0:01 | 46107.5945 | 65.6 | 68.6 | 60.5 | 58.6 | 62.5 | 56.7 | 58.2 | 55.9 | 52.9 | 49.6 | 51.1 | 47.7 | 46.6 | 48.3 | 48 | 45.2 | 44.2 | 42.4 | 41.8 | 40.8 | 40 | 38.3 | 38.1 | 37.9 | 35.2 | 44.7 | 39.6 | 55.2 | 1
654 | 0:01 | 46107.5958 | 60.5 | 57.6 | 55.9 | 56.6 | 54.1 | 50.4 | 49.7 | 48.2 | 47.5 | 43.3 | 41.5 | 42.9 | 41.7 | 41.3 | 44.7 | 43.2 | 42.9 | 41.5 | 40.1 | 39.9 | 39.9 | 39.4 | 39.2 | 38.3 | 36.4 | 35.1 | 31.5 | 52.3 | 1
655 | 0:01 | 46107.6019 | 68.8 | 62.7 | 62.8 | 61.6 | 51.9 | 56.7 | 50.9 | 60.7 | 58.6 | 54.8 | 52.7 | 58.2 | 56.5 | 58.4 | 56.6 | 56 | 55.7 | 53.7 | 51.4 | 50.4 | 46.6 | 45.1 | 44.8 | 37.3 | 36.9 | 35.6 | 32.4 | 63.9 | 1
656 | 0:01 | 46107.6039 | 64.7 | 66 | 66 | 60.5 | 57.4 | 53.8 | 54.6 | 57.6 | 62.2 | 53.2 | 51.5 | 51.2 | 49.1 | 50.5 | 51.2 | 55.1 | 58 | 66.5 | 69.8 | 50.9 | 45.3 | 48.3 | 37.8 | 34.5 | 31.8 | 30.1 | 28.4 | 72.6 | 1
657 | 0:00 | 46107.6042 | 64.6 | 66.6 | 65.4 | 59.7 | 55.7 | 53.8 | 55.7 | 58.8 | 62.5 | 52.9 | 50.2 | 49.9 | 48.9 | 49.8 | 49.6 | 54.9 | 57.9 | 59 | 57.5 | 47.5 | 44 | 41.2 | 36.9 | 32.2 | 29.2 | 27.7 | 26.4 | 64.6 | 1
658 | 0:01 | 46107.6051 | 65.5 | 65.4 | 66.2 | 61.7 | 58.3 | 55.2 | 56.2 | 58.3 | 62.2 | 54.1 | 52 | 53 | 50.5 | 50.8 | 51.7 | 53.8 | 53.5 | 51.9 | 50.3 | 47 | 43.5 | 41.1 | 37.6 | 35.1 | 33.5 | 32.1 | 30.1 | 60.9 | 1
659 | 0:01 | 46107.6087 | 59.8 | 59 | 56.2 | 52.5 | 50.3 | 57.9 | 52.2 | 50.3 | 47.9 | 46.9 | 46.6 | 52.4 | 47.1 | 45.3 | 46.5 | 44 | 41.8 | 41.1 | 40.9 | 40.9 | 40.4 | 39.9 | 39.9 | 39.4 | 38.3 | 36.7 | 34.8 | 54.2 | 1
660 | 0:01 | 46107.6102 | 61.7 | 60.2 | 58 | 54.8 | 51.7 | 60.1 | 52.6 | 48.5 | 46.8 | 44.8 | 43.2 | 43.8 | 45.6 | 45.9 | 44.9 | 40.3 | 39.4 | 41.2 | 40.5 | 38.1 | 37.6 | 36.5 | 33.7 | 32.9 | 31.7 | 29 | 26.8 | 51.6 | 1
661 | 0:01 | 46107.6134 | 59.1 | 67.2 | 65.3 | 61.8 | 60.6 | 63 | 61.6 | 65.9 | 69 | 81 | 73.3 | 71.1 | 71.6 | 69.8 | 68.9 | 67.3 | 69 | 69.8 | 69.5 | 69.8 | 69.7 | 68.8 | 67.6 | 65.7 | 63.4 | 62.9 | 58.1 | 80.6 | 1
662 | 0:01 | 46107.6163 | 53.5 | 53.6 | 51.4 | 50.4 | 50.9 | 51.8 | 53.5 | 50.2 | 44.2 | 43.5 | 44 | 46.1 | 43.9 | 47.1 | 41.2 | 39.9 | 38.9 | 37.3 | 37.2 | 37.8 | 37.7 | 37.1 | 36.7 | 35.8 | 33.8 | 29.9 | 25.7 | 50.9 | 1
663 | 0:01 | 46107.6173 | 53.7 | 54.7 | 54 | 55 | 53.2 | 53 | 55.8 | 52.6 | 51 | 49.3 | 50.1 | 46.8 | 44.4 | 46.1 | 44 | 42 | 41.7 | 41.5 | 42.2 | 42.8 | 44 | 43.2 | 42.8 | 42.7 | 40 | 33.5 | 27.6 | 54.7 | 1
664 | 0:01 | 46107.6183 | 55.9 | 55.4 | 53.5 | 54.5 | 56.3 | 52.8 | 51.2 | 47.2 | 47 | 45.4 | 45.4 | 45.8 | 44 | 44.9 | 42.5 | 41.8 | 39.9 | 38.2 | 37.8 | 37.3 | 36.4 | 35.3 | 34.6 | 33.8 | 31.9 | 29 | 26.2 | 50.7 | 1
666 | 0:00 | 46107.6649 | 52.9 | 40.2 | 44.9 | 36.7 | 38.4 | 38.1 | 42.1 | 36.2 | 40.3 | 41.2 | 40.4 | 35.7 | 38.5 | 36.4 | 33.9 | 32.5 | 32.4 | 32.3 | 32.3 | 33.3 | 31.8 | 30.8 | 30.1 | 28.4 | 26.8 | 24.9 | 22.8 | 44.2 | 1
[32 empty] | Record | Start Time | E | H | K | N | Q | T | W | Z | AC
L619 | 0:00 | 46107.4102 |  | 63.9219 |  |  | 76.2588 |  |  | 61.1578 |  |  | 59.8458 |  |  | 58.5526 |  |  | 59.0421 |  |  | 57.8239 |  |  | 50.4371 |  |  | 40.5242 |  | 63.5 |  | L619 | 46107.4102 | 63.9219 | 76.2588 | 61.1578 | 59.8458 | 58.5526 | 59.0421 | 57.8239 | 50.4371 | 40.5242 | 63.5
L620 | 0:01 | 46107.4103 |  | 66.216 |  |  | 76.2023 |  |  | 72.7653 |  |  | 76.7015 |  |  | 75.2577 |  |  | 72.8653 |  |  | 72.7514 |  |  | 68.4013 |  |  | 63.3681 |  | 78.7 |  | L620 | 46107.4103 | 66.216 | 76.2023 | 72.7653 | 76.7015 | 75.2577 | 72.8653 | 72.7514 | 68.4013 | 63.3681 | 78.7
L621 | 0:01 | 46107.4112 |  | 66.3371 |  |  | 67.8076 |  |  | 73.0631 |  |  | 71.4887 |  |  | 69.8217 |  |  | 67.3895 |  |  | 66.2085 |  |  | 62.5033 |  |  | 56.6744 |  | 73 |  | L621 | 46107.4112 | 66.3371 | 67.8076 | 73.0631 | 71.4887 | 69.8217 | 67.3895 | 66.2085 | 62.5033 | 56.6744 | 73
L622 | 0:01 | 46107.4121 |  | 73.2299 |  |  | 79.0281 |  |  | 72.283 |  |  | 73.6839 |  |  | 72.5982 |  |  | 68.1473 |  |  | 67.8759 |  |  | 63.3153 |  |  | 58.8474 |  | 74.7 |  | L622 | 46107.4121 | 73.2299 | 79.0281 | 72.283 | 73.6839 | 72.5982 | 68.1473 | 67.8759 | 63.3153 | 58.8474 | 74.7
L623 | 0:01 | 46107.4144 |  | 81.4048 |  |  | 91.2243 |  |  | 87.0208 |  |  | 97.7072 |  |  | 91.5716 |  |  | 89.5794 |  |  | 88.2724 |  |  | 84.6266 |  |  | 80.1831 |  | 95.3 |  | L623 | 46107.4144 | 81.4048 | 91.2243 | 87.0208 | 97.7072 | 91.5716 | 89.5794 | 88.2724 | 84.6266 | 80.1831 | 95.3
L624 | 0:01 | 46107.4152 |  | 86.0882 |  |  | 102.0064 |  |  | 96.8496 |  |  | 93.4083 |  |  | 92.6439 |  |  | 91.2003 |  |  | 89.355 |  |  | 87.5528 |  |  | 85.1312 |  | 96.6 |  | L624 | 46107.4152 | 86.0882 | 102.0064 | 96.8496 | 93.4083 | 92.6439 | 91.2003 | 89.355 | 87.5528 | 85.1312 | 96.6
L625 | 0:01 | 46107.4161 |  | 75.5809 |  |  | 81.0552 |  |  | 83.9814 |  |  | 86.4699 |  |  | 89.7947 |  |  | 84.493 |  |  | 83.1171 |  |  | 79.5522 |  |  | 75.6031 |  | 90.7 |  | L625 | 46107.4161 | 75.5809 | 81.0552 | 83.9814 | 86.4699 | 89.7947 | 84.493 | 83.1171 | 79.5522 | 75.6031 | 90.7
L626 | 0:01 | 46107.4187 |  | 88.8967 |  |  | 96.7921 |  |  | 95.4718 |  |  | 90.3257 |  |  | 89.2712 |  |  | 80.8154 |  |  | 74.9753 |  |  | 68.1601 |  |  | 64.7 |  | 89 |  | L626 | 46107.4187 | 88.8967 | 96.7921 | 95.4718 | 90.3257 | 89.2712 | 80.8154 | 74.9753 | 68.1601 | 64.7 | 89
L627 | 0:01 | 46107.4198 |  | 87.9015 |  |  | 100.0778 |  |  | 94.7335 |  |  | 89.8299 |  |  | 85.9506 |  |  | 77.8724 |  |  | 74.6193 |  |  | 69.5493 |  |  | 65.0717 |  | 86.9 |  | L627 | 46107.4198 | 87.9015 | 100.0778 | 94.7335 | 89.8299 | 85.9506 | 77.8724 | 74.6193 | 69.5493 | 65.0717 | 86.9
L628 | 0:01 | 46107.421 |  | 86.85 |  |  | 95.4613 |  |  | 95.3441 |  |  | 85.5029 |  |  | 75.64 |  |  | 71.5129 |  |  | 64.0008 |  |  | 60.7581 |  |  | 55.0825 |  | 83.1 |  | L628 | 46107.421 | 86.85 | 95.4613 | 95.3441 | 85.5029 | 75.64 | 71.5129 | 64.0008 | 60.7581 | 55.0825 | 83.1
L629 | 0:01 | 46107.4254 |  | 56.3856 |  |  | 56.183 |  |  | 65.3177 |  |  | 66.0436 |  |  | 62.5999 |  |  | 58.4276 |  |  | 45.468 |  |  | 41.676 |  |  | 39.6336 |  | 63.2 |  | L629 | 46107.4254 | 56.3856 | 56.183 | 65.3177 | 66.0436 | 62.5999 | 58.4276 | 45.468 | 41.676 | 39.6336 | 63.2
L630 | 0:01 | 46107.4272 |  | 62.0659 |  |  | 62.1529 |  |  | 60.5618 |  |  | 62.754 |  |  | 60.849 |  |  | 57.3268 |  |  | 49.1581 |  |  | 47.1476 |  |  | 38.6051 |  | 61.7 |  | L630 | 46107.4272 | 62.0659 | 62.1529 | 60.5618 | 62.754 | 60.849 | 57.3268 | 49.1581 | 47.1476 | 38.6051 | 61.7
L631 | 0:01 | 46107.4307 |  | 58.8158 |  |  | 51.7187 |  |  | 50.7484 |  |  | 52.1311 |  |  | 53.6791 |  |  | 48.7354 |  |  | 51.3684 |  |  | 47.2475 |  |  | 38.5684 |  | 56.6 |  | L631 | 46107.4307 | 58.8158 | 51.7187 | 50.7484 | 52.1311 | 53.6791 | 48.7354 | 51.3684 | 47.2475 | 38.5684 | 56.6
L632 | 0:01 | 46107.432 |  | 58.7437 |  |  | 56.5581 |  |  | 52.8702 |  |  | 51.9216 |  |  | 50.2519 |  |  | 50.5236 |  |  | 51.7824 |  |  | 49.7113 |  |  | 42.8651 |  | 57.1 |  | L632 | 46107.432 | 58.7437 | 56.5581 | 52.8702 | 51.9216 | 50.2519 | 50.5236 | 51.7824 | 49.7113 | 42.8651 | 57.1
L633 | 0:01 | 46107.4356 |  | 58.4048 |  |  | 57.7088 |  |  | 55.2939 |  |  | 57.9773 |  |  | 52.6799 |  |  | 45.6604 |  |  | 45.6308 |  |  | 40.8733 |  |  | 34.0028 |  | 54.6 |  | L633 | 46107.4356 | 58.4048 | 57.7088 | 55.2939 | 57.9773 | 52.6799 | 45.6604 | 45.6308 | 40.8733 | 34.0028 | 54.6
L634 | 0:01 | 46107.4377 |  | 58.2394 |  |  | 57.0914 |  |  | 55.4051 |  |  | 52.3528 |  |  | 47.925 |  |  | 50.4806 |  |  | 46.3459 |  |  | 39.7098 |  |  | 33.3406 |  | 53.8 |  | L634 | 46107.4377 | 58.2394 | 57.0914 | 55.4051 | 52.3528 | 47.925 | 50.4806 | 46.3459 | 39.7098 | 33.3406 | 53.8
L635 | 0:01 | 46107.4487 |  | 63.6751 |  |  | 59.7322 |  |  | 59.6893 |  |  | 77.2011 |  |  | 62.3856 |  |  | 58.0895 |  |  | 54.9724 |  |  | 55.7797 |  |  | 59.3198 |  | 68.5 |  | L635 | 46107.4487 | 63.6751 | 59.7322 | 59.6893 | 77.2011 | 62.3856 | 58.0895 | 54.9724 | 55.7797 | 59.3198 | 68.5
L636 | 0:00 | 46107.4494 |  | 59.0514 |  |  | 58.2506 |  |  | 59.7282 |  |  | 78.6419 |  |  | 58.5394 |  |  | 57.333 |  |  | 52.4008 |  |  | 54.3965 |  |  | 55.2197 |  | 68.4 |  | L636 | 46107.4494 | 59.0514 | 58.2506 | 59.7282 | 78.6419 | 58.5394 | 57.333 | 52.4008 | 54.3965 | 55.2197 | 68.4
L637 | 0:01 | 46107.4494 |  | 57.5028 |  |  | 56.1415 |  |  | 57.6121 |  |  | 63.4811 |  |  | 67.308 |  |  | 63.2676 |  |  | 59.886 |  |  | 57.0325 |  |  | 51.2248 |  | 68.5 |  | L637 | 46107.4494 | 57.5028 | 56.1415 | 57.6121 | 63.4811 | 67.308 | 63.2676 | 59.886 | 57.0325 | 51.2248 | 68.5
L638 | 0:01 | 46107.4583 |  | 63.785 |  |  | 60.2569 |  |  | 68.0739 |  |  | 64.2473 |  |  | 64.0806 |  |  | 60.8575 |  |  | 55.9382 |  |  | 45.3051 |  |  | 38.6945 |  | 65.4 |  | L638 | 46107.4583 | 63.785 | 60.2569 | 68.0739 | 64.2473 | 64.0806 | 60.8575 | 55.9382 | 45.3051 | 38.6945 | 65.4
L639 | 0:01 | 46107.4594 |  | 64.4059 |  |  | 61.4033 |  |  | 71.9262 |  |  | 67.8211 |  |  | 66.6687 |  |  | 64.0058 |  |  | 59.3023 |  |  | 51.8827 |  |  | 43.1275 |  | 68.4 |  | L639 | 46107.4594 | 64.4059 | 61.4033 | 71.9262 | 67.8211 | 66.6687 | 64.0058 | 59.3023 | 51.8827 | 43.1275 | 68.4
L640 | 0:01 | 46107.4685 |  | 58.5693 |  |  | 52.7185 |  |  | 48.9811 |  |  | 48.8171 |  |  | 56.7755 |  |  | 51.2965 |  |  | 52.2811 |  |  | 48.42 |  |  | 36.9233 |  | 58.3 |  | L640 | 46107.4685 | 58.5693 | 52.7185 | 48.9811 | 48.8171 | 56.7755 | 51.2965 | 52.2811 | 48.42 | 36.9233 | 58.3
L641 | 0:01 | 46107.5325 |  | 73.3339 |  |  | 59.1041 |  |  | 56.0034 |  |  | 56.1039 |  |  | 54.4561 |  |  | 52.04 |  |  | 48.1139 |  |  | 39.6491 |  |  | 31.7079 |  | 56.5 |  | L641 | 46107.5325 | 73.3339 | 59.1041 | 56.0034 | 56.1039 | 54.4561 | 52.04 | 48.1139 | 39.6491 | 31.7079 | 56.5
L642 | 0:01 | 46107.5334 |  | 73.7977 |  |  | 63.2887 |  |  | 54.2139 |  |  | 52.2918 |  |  | 49.6479 |  |  | 48.9311 |  |  | 43.8937 |  |  | 38.9479 |  |  | 28.7532 |  | 52.9 |  | L642 | 46107.5334 | 73.7977 | 63.2887 | 54.2139 | 52.2918 | 49.6479 | 48.9311 | 43.8937 | 38.9479 | 28.7532 | 52.9
L643 | 0:01 | 46107.5344 |  | 69.7892 |  |  | 58.0636 |  |  | 55.4379 |  |  | 52.3204 |  |  | 50.6768 |  |  | 52.6339 |  |  | 48.172 |  |  | 40.9868 |  |  | 34.2296 |  | 55.7 |  | L643 | 46107.5344 | 69.7892 | 58.0636 | 55.4379 | 52.3204 | 50.6768 | 52.6339 | 48.172 | 40.9868 | 34.2296 | 55.7
L644 | 0:01 | 46107.5437 |  | 61.9895 |  |  | 63.745 |  |  | 62.5408 |  |  | 65.4223 |  |  | 60.61 |  |  | 60.343 |  |  | 57.9878 |  |  | 53.4457 |  |  | 39.5317 |  | 64.8 |  | L644 | 46107.5437 | 61.9895 | 63.745 | 62.5408 | 65.4223 | 60.61 | 60.343 | 57.9878 | 53.4457 | 39.5317 | 64.8
L645 | 0:01 | 46107.5526 |  | 66.9052 |  |  | 61.7379 |  |  | 55.5193 |  |  | 51.4336 |  |  | 51.9255 |  |  | 48.293 |  |  | 43.5748 |  |  | 38.578 |  |  | 30.7639 |  | 52.9 |  | L645 | 46107.5526 | 66.9052 | 61.7379 | 55.5193 | 51.4336 | 51.9255 | 48.293 | 43.5748 | 38.578 | 30.7639 | 52.9
L646 | 0:01 | 46107.5816 |  | 70.9227 |  |  | 63.7308 |  |  | 57.3503 |  |  | 52.3452 |  |  | 49.3748 |  |  | 49.3484 |  |  | 47.6041 |  |  | 44.743 |  |  | 42.574 |  | 54.6 |  | L646 | 46107.5816 | 70.9227 | 63.7308 | 57.3503 | 52.3452 | 49.3748 | 49.3484 | 47.6041 | 44.743 | 42.574 | 54.6
L647 | 0:01 | 46107.5831 |  | 69.7034 |  |  | 62.1923 |  |  | 56.6332 |  |  | 51.5918 |  |  | 49.0659 |  |  | 50.5677 |  |  | 45.1982 |  |  | 42.0262 |  |  | 39.4048 |  | 54 |  | L647 | 46107.5831 | 69.7034 | 62.1923 | 56.6332 | 51.5918 | 49.0659 | 50.5677 | 45.1982 | 42.0262 | 39.4048 | 54
L648 | 0:01 | 46107.5845 |  | 73.6507 |  |  | 64.87 |  |  | 59.4659 |  |  | 57.5282 |  |  | 53.562 |  |  | 55.3723 |  |  | 52.9952 |  |  | 50.0516 |  |  | 45.8381 |  | 59.7 |  | L648 | 46107.5845 | 73.6507 | 64.87 | 59.4659 | 57.5282 | 53.562 | 55.3723 | 52.9952 | 50.0516 | 45.8381 | 59.7
L649 | 0:01 | 46107.5856 |  | 68.5225 |  |  | 60.4021 |  |  | 56.6804 |  |  | 54.1765 |  |  | 50.586 |  |  | 53.8949 |  |  | 50.3039 |  |  | 47.4906 |  |  | 44.4708 |  | 57.5 |  | L649 | 46107.5856 | 68.5225 | 60.4021 | 56.6804 | 54.1765 | 50.586 | 53.8949 | 50.3039 | 47.4906 | 44.4708 | 57.5
L650 | 0:01 | 46107.5864 |  | 76.2765 |  |  | 68.3101 |  |  | 62.4423 |  |  | 60.7747 |  |  | 57.0454 |  |  | 59.7056 |  |  | 55.7209 |  |  | 50.6295 |  |  | 44.5109 |  | 62.8 |  | L650 | 46107.5864 | 76.2765 | 68.3101 | 62.4423 | 60.7747 | 57.0454 | 59.7056 | 55.7209 | 50.6295 | 44.5109 | 62.8
L651 | 0:01 | 46107.5919 |  | 60.2144 |  |  | 58.3104 |  |  | 54.7731 |  |  | 52.6759 |  |  | 53.3897 |  |  | 53.2619 |  |  | 50.1578 |  |  | 46.857 |  |  | 41.2339 |  | 57.3 |  | L651 | 46107.5919 | 60.2144 | 58.3104 | 54.7731 | 52.6759 | 53.3897 | 53.2619 | 50.1578 | 46.857 | 41.2339 | 57.3
L652 | 0:01 | 46107.5929 |  | 65.943 |  |  | 59.2276 |  |  | 54.0824 |  |  | 54.8325 |  |  | 54.7639 |  |  | 48.4534 |  |  | 45.9952 |  |  | 44.8729 |  |  | 41.2423 |  | 55.3 |  | L652 | 46107.5929 | 65.943 | 59.2276 | 54.0824 | 54.8325 | 54.7639 | 48.4534 | 45.9952 | 44.8729 | 41.2423 | 55.3
L653 | 0:01 | 46107.5938 |  | 70.7908 |  |  | 64.7282 |  |  | 60.9507 |  |  | 54.4546 |  |  | 52.4653 |  |  | 48.8533 |  |  | 45.7006 |  |  | 42.8743 |  |  | 46.2266 |  | 55.2 |  | L653 | 46107.5938 | 70.7908 | 64.7282 | 60.9507 | 54.4546 | 52.4653 | 48.8533 | 45.7006 | 42.8743 | 46.2266 | 55.2
L654 | 0:01 | 46107.5951 |  | 63.1942 |  |  | 59.1581 |  |  | 53.3371 |  |  | 47.4039 |  |  | 47.6187 |  |  | 47.3653 |  |  | 44.7389 |  |  | 43.7636 |  |  | 39.549 |  | 52.3 |  | L654 | 46107.5951 | 63.1942 | 59.1581 | 53.3371 | 47.4039 | 47.6187 | 47.3653 | 44.7389 | 43.7636 | 39.549 | 52.3
L655 | 0:01 | 46107.6012 |  | 70.5512 |  |  | 63.1556 |  |  | 63.0586 |  |  | 60.6028 |  |  | 62.0292 |  |  | 60.0176 |  |  | 54.6745 |  |  | 48.3206 |  |  | 40.1142 |  | 63.9 |  | L655 | 46107.6012 | 70.5512 | 63.1556 | 63.0586 | 60.6028 | 62.0292 | 60.0176 | 54.6745 | 48.3206 | 40.1142 | 63.9
L656 | 0:01 | 46107.6033 |  | 70.3796 |  |  | 62.8136 |  |  | 64.0199 |  |  | 56.8306 |  |  | 55.123 |  |  | 67.3411 |  |  | 69.8708 |  |  | 48.8339 |  |  | 35.0903 |  | 72.6 |  | L656 | 46107.6033 | 70.3796 | 62.8136 | 64.0199 | 56.8306 | 55.123 | 67.3411 | 69.8708 | 48.8339 | 35.0903 | 72.6
L657 | 0:00 | 46107.6041 |  | 70.3831 |  |  | 61.8884 |  |  | 64.6365 |  |  | 55.9925 |  |  | 54.2214 |  |  | 62.3552 |  |  | 58.0868 |  |  | 42.9535 |  |  | 32.6884 |  | 64.6 |  | L657 | 46107.6041 | 70.3831 | 61.8884 | 64.6365 | 55.9925 | 54.2214 | 62.3552 | 58.0868 | 42.9535 | 32.6884 | 64.6
L658 | 0:01 | 46107.6044 |  | 70.486 |  |  | 63.9556 |  |  | 64.3973 |  |  | 57.8891 |  |  | 55.8017 |  |  | 57.9144 |  |  | 52.5445 |  |  | 43.3991 |  |  | 36.8876 |  | 60.9 |  | L658 | 46107.6044 | 70.486 | 63.9556 | 64.3973 | 57.8891 | 55.8017 | 57.9144 | 52.5445 | 43.3991 | 36.8876 | 60.9
L659 | 0:01 | 46107.608 |  | 63.357 |  |  | 59.55 |  |  | 55.2475 |  |  | 54.2889 |  |  | 51.134 |  |  | 47.254 |  |  | 45.5109 |  |  | 44.5109 |  |  | 41.6011 |  | 54.2 |  | L659 | 46107.608 | 63.357 | 59.55 | 55.2475 | 54.2889 | 51.134 | 47.254 | 45.5109 | 44.5109 | 41.6011 | 54.2
L660 | 0:01 | 46107.6095 |  | 64.993 |  |  | 61.6826 |  |  | 54.7803 |  |  | 48.7553 |  |  | 50.2578 |  |  | 45.1332 |  |  | 43.6979 |  |  | 39.4255 |  |  | 34.3966 |  | 51.6 |  | L660 | 46107.6095 | 64.993 | 61.6826 | 54.7803 | 48.7553 | 50.2578 | 45.1332 | 43.6979 | 39.4255 | 34.3966 | 51.6
L661 | 0:01 | 46107.6127 |  | 69.754 |  |  | 66.681 |  |  | 71.2317 |  |  | 82.0454 |  |  | 75.0197 |  |  | 73.5914 |  |  | 74.4397 |  |  | 72.3187 |  |  | 66.7972 |  | 80.6 |  | L661 | 46107.6127 | 69.754 | 66.681 | 71.2317 | 82.0454 | 75.0197 | 73.5914 | 74.4397 | 72.3187 | 66.7972 | 80.6
L662 | 0:01 | 46107.6156 |  | 57.7159 |  |  | 55.8437 |  |  | 55.5009 |  |  | 49.4569 |  |  | 49.4947 |  |  | 43.5993 |  |  | 42.3457 |  |  | 41.3379 |  |  | 35.7375 |  | 50.9 |  | L662 | 46107.6156 | 57.7159 | 55.8437 | 55.5009 | 49.4569 | 49.4947 | 43.5993 | 42.3457 | 41.3379 | 35.7375 | 50.9
L663 | 0:01 | 46107.6166 |  | 58.925 |  |  | 58.6015 |  |  | 58.3762 |  |  | 53.7163 |  |  | 49.7034 |  |  | 46.5094 |  |  | 47.8368 |  |  | 47.6766 |  |  | 41.0769 |  | 54.7 |  | L663 | 46107.6166 | 58.925 | 58.6015 | 58.3762 | 53.7163 | 49.7034 | 46.5094 | 47.8368 | 47.6766 | 41.0769 | 54.7
L664 | 0:01 | 46107.6176 |  | 59.8211 |  |  | 59.5374 |  |  | 53.7 |  |  | 50.3087 |  |  | 48.6808 |  |  | 44.9852 |  |  | 41.9759 |  |  | 39.3808 |  |  | 34.4091 |  | 50.7 |  | L664 | 46107.6176 | 59.8211 | 59.5374 | 53.7 | 50.3087 | 48.6808 | 44.9852 | 41.9759 | 39.3808 | 34.4091 | 50.7
L666 | 0:00 | 46107.6646 |  | 53.7357 |  |  | 42.5653 |  |  | 44.9279 |  |  | 44.4502 |  |  | 41.4299 |  |  | 37.172 |  |  | 37.2833 |  |  | 34.6499 |  |  | 29.9043 |  | 44.2 |  | L666 | 46107.6646 | 53.7357 | 42.5653 | 44.9279 | 44.4502 | 41.4299 | 37.172 | 37.2833 | 34.6499 | 29.9043 | 44.2
Potential tonality check (at source)
|  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
L620
L621
L622
L623 | [11 empty] | X
L624
L625
L626
L627 | [5 empty] | X
L628
L629 | [8 empty] | X
L630
L631
L632
L633
L634
L635 | [11 empty] | X | [15 empty] | X
L636 | [11 empty] | X | [15 empty] | X
L637
L638
L639
L640 | [15 empty] | X
L641
L642
L643
L644
L645
L646
L647
L648
L649
L650
L651
L652
L653 | [27 empty] | X
L654
L655
L656
L658
L659
L660
L661
L662
L663
L664
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Possible tone at 50/100/200 Hz

## Backup Gen & Fire pumps
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
Backup generator & fire water pump area | Fire fighting water pumps - Electric pump (South) | 1 | L620 | 26/03/2026 | 9:51 | 1 minute | 80.2 | 78.73 | 79.7 | 77.5 | Dominant noise source - double door access - one door left open to simulate worst case | One pump in operation at one time - no access to north side of unit
| Fire fighting water pumps - Electric pump (East) | 2 | L621 | 26/03/2026 | 9:52 | 1 minute | 74.14 | 73.01 | 73.8 | 72.1 | Dominant noise source - one door left open - measurement taken 1m from east louvre
| Fire fighting water pumps - Electric pump (West) | 3 | L622 | 26/03/2026 | 9:53 | 1 minute | 76.38 | 74.69 | 75.6 | 74 | Dominant noise source / some RTN from Cowpen Lane - one door left open - measurement taken 1m from west louvre
| Fire fighting water pumps - Diesel pump (South) | 4 | L623 | 26/03/2026 | 9:57 | 1 minute | 96.51 | 95.29 | 95.9 | 94.3 | Dominant noise source - double door access - one door left open to simulate worst case | One pump in operation at one time - no access to north side of unit
| Fire fighting water pumps - Diesel pump (East) | 5 | L624 | 26/03/2026 | 9:58 | 1 minute | 97.58 | 96.56 | 96.9 | 96 | Dominant noise source - one door left open - measurement taken 1m from east louvre
| Fire fighting water pumps - Diesel pump (West) | 6 | L625 | 26/03/2026 | 09:59 | 1 minute | 91.81 | 90.67 | 91.6 | 89.6 | Dominant noise source - one door left open - measurement taken 1m from west louvre
| Diesel backup generator (West) | 7 | L626 | 26/03/2026 | 10:03 | 1 minute | 90.99 | 89.01 | 89.9 | 88 | Dominant noise source - measurement taken 1m from west louvres | Only diesel generator running - no access to south side of unit
| Diesel backup generator (East) | 8 | L627 | 26/03/2026 | 10:04 | 1 minute | 88.68 | 86.85 | 87.9 | 85.1 | Dominant noise source - measurement taken 1m from east louvre
| Diesel backup generator (North) | 9 | L628 | 26/03/2026 | 10:06 | 1 minute | 84.67 | 83.05 | 84 | 82 | Dominant noise source - measurement taken 1m from north louvres
[5 empty] | 1 & 4 |  |  |  |  | 7
[5 empty] | 2 & 5 |  |  |  |  | 8 | Missing
9
3 & 6
Weather:
11oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 |  | SLM cal expiry: 23/05/2026 |  | Cert: UCRT24/1777
Wind: up to 0.4ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 |  | Cal cal expiry: 29/07/2026 |  | Cert: CE-REP-10992

## Northern Facade
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS |  |  | 634 : Total results
Northern Façade | Transformer room (internal) | 10 | L629 | 26/03/2026 | 10:12 | 1 minute | 68.44 | 63.21 | 64.2 | 62.1 | Dominant noise source - reverberant level uniform throughout space
| Transformer room (external - 1m from door & façade) | 11 | L630 | 26/03/2026 | 10:15 | 1 minute | 76.08 | 61.67 | 63.7 | 56.5 | Internal noise inaudible - road traffic noise from Cowpen Lane dominant | [6 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
| LV Switch room (internal) | 12 | L631 | 26/03/2026 | 10:20 | 1 minute | 77.65 | 56.61 | 57 | 44.5 | Dominant noise source - reverberant level uniform throughout space | [6 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
| LV Switch room (external - 1m from door & façade) | 13 | L632 | 26/03/2026 | 10:22 | 1 minute | 78.17 | 57.08 | 56.1 | 46.4 | Internal noise inaudible - road traffic noise from Cowpen Lane dominant |  |  | No. | Start date & time | Duration | Name |  |  | L10 | L90
| Compressor room (internal) | 14 | L633 | 26/03/2026 | 10:27 | 1 minute | 64.52 | 54.61 | 55.9 | 51.6 | Dominant noise source - reverberant level uniform throughout space |  |  | 1 | 26/03/2026 10:30:18.000 | 00:01:00.000 | Integration period 1 m | 68.58 | 53.77 | 55.4 | 49.3
| Compressor room (external - 1m from louvres) | 15 | L634 | 26/03/2026 | 10:30 | 1 minute | 68.58 | 53.77 | 55.4 | 49.3 | Internal noise inaudible - road traffic noise from Cowpen Lane dominant
| Cold water distribution tanks & pumps | 16 | Unable to be manually operated due to current operational condition | [7 empty] | With no internal or external measurements done , photo of pump manufacturer taken |  | Grundfos CRIE 15-3 A-FGJ-A-E-HQQE
[5 empty] | 10 |  |  |  |  | 13 |  | 16
[5 empty] | 11 |  |  |  |  | 14 |  | 16
[5 empty] | 12 |  |  |  |  | 15 |  | 16
Weather: | [11 empty] | 16A
11oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 |  | SLM cal expiry: 23/05/2026 |  | Cert: UCRT24/1777
Wind: up to 2.3ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 |  | Cal cal expiry: 29/07/2026 |  | Cert: CE-REP-10992
Note on S11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Grundfos CRIE 15-3 A-FGJ-A-E-HQQE (Model 99071547) is a vertical, multistage, E-pump with an integrated frequency converter (IE5 motor). Designed for 15 nominal flow and 3 stages, it features 316/304 stainless steel construction, DIN/ANSI/JIS flange connections, and EPDM rubber components, designed for high-efficiency, variable-speed pressure boosting. Detailed Code Breakdown CRIE: Vertical multistage pump with an integrated frequency converter (E-pump) and stainless steel wetted parts (AISI 304/316). 15: Rated Flow in m3/h. 3: Number of Impellers / stages. A: Pump Version (A = Basic version). FGJ: Pipe Connection (DIN / ANSI / JIS flange, DN 50 / 2 inch). A: Materials (A = Stainless steel 1.4408/AISI 316 base, 1.4301/AISI 304 components). E: Rubber Material (EPDM - Ethylene Propylene Diene Monomer, suitable for water, not oil). HQQE: Shaft Seal (H = Silicon Carbide/Silicon Carbide seal face, Q = Silicon Carbide seat, E = EPDM rubber). Grundfos Product Center Key Technical Specifications Performance: Nominal flow 15-21 m3/h, Maximum head approx. 46m - 61m. Motor: 3-phase, 4.0 kW, 380-500 V, Integrated IE5 frequency converter. Connections: DN50 / 2" flange, PN 25/300 lb. Applications: Industrial water treatment, process water, pressure boosting, HVAC. Seal & Temp: HQQE seal, rated for liquid temperatures from -20 to 120C Reply: Main noise source is understood to be the motor itself. Screenshot 16A taken from: https://product-selection.grundfos.com/content/dam/global/page-assets/products-and-services/products/documents/ind-mge-tech-brochure-gpu.pdf (highlighted value for the expected motor of this pump)

## Segregated Waste Pit
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
Segregated Waste Pit | Extract vents & relief lines (west) | 17 | L638 | 26/03/2026 | 10:59 | 1 minute | 68.26 | 65.35 | 67.2 | 59.1 | Extract vent dominant with some external site noise present | Only 1 vent measured. Unable to complete orientation of vent as platfom had wet paint. Other vent similar in noise character and amplitude. Relief line not audible (green curve) | Vent-Axia RCZ300
| Extract vents & relief lines (north) | 18 | L639 | 26/03/2026 | 11:01 | 1 minute | 72.87 | 68.41 | 69.7 | 66.1 | Extract vent dominant with some external site noise present
17
18
Weather:
12oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 |  | SLM cal expiry: 23/05/2026 |  | Cert: UCRT24/1777
Wind: up to 1.4ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 |  | Cal cal expiry: 29/07/2026 |  | Cert: CE-REP-10992

## Liquid Waste Building
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
Liquid Waste Building | Internal waste pumps | 19 | L636 | 26/03/2026 | 10:47 | 1 minute | 69.9 | 68.38 | 70 | 65.5 | Dominant noise source - reverberant level uniform throughout space
| AHU fresh air inlet & vent / grille (external south façade) | 20 | Nothing audible - site noise and RTN dominant | [7 empty] | No noise audible - site noise and road traffic noise from Cowpen Lane dominant
| Roof relief vents / extract fan discharge (10m away) | 21 | L641 | 26/03/2026 | 12:46 | 1 minute | 67.08 | 56.51 | 58.9 | 51.7 | No noise audible - road traffic noise from Cowpen Lane dominant | 3B boom platform unable to track over north façade ground, therefore measurements taken from south roof area
| Roof relief vents / extract fan discharge (5m away) | 22 | L642 | 26/03/2026 | 12:48 | 1 minute | 70.57 | 52.85 | 55.5 | 47.9 | No noise audible - road traffic noise from Cowpen Lane dominant
| AHU Exhaust | 23 | L643 | 26/03/2026 | 12:49 | 1 minute | 74.97 | 55.67 | 56.1 | 50.5 | Minimal noise - Road traffic noise from Cowpen Lane dominant
| DX cooling unit to rear | 24 | Unable to be manually operated due to current operational building condition | [7 empty] | Photo of unit manufacturer taken for source data - Daikin Sky Air R32 Alpha
[5 empty] | 19 |  |  |  |  | 22 | missing
23
[5 empty] | 20 | Missing
[5 empty] | 21 |  |  |  |  | 24
Weather:
12oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 |  | SLM cal expiry: 23/05/2026 |  | Cert: UCRT24/1777
Wind: up to 1.7ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 |  | Cal cal expiry: 29/07/2026 |  | Cert: CE-REP-10992

## East Facade
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
East Façade | Room extract exhaust from Cryostore | 25 | L644 | 26/03/2026 | 13:02 | 1 minute | 75.66 | 64.83 | 65.8 | 63 | Extract noise audible - some extreneous noise from other site activities noted
| Room extract exhaust (north end) | 26 | L645 | 26/03/2026 | 13:15 | 1 minute | 72.64 | 52.9 | 52.2 | 49 | No noise audible - extreneous noise from other site activities dominant
| Supply air to cryostore AHU | 27 | Unable to measure - 3b boom unable to reach area due to ground obtacles | [7 empty] | N/A
| AHU extract from stair core | 28 | Unable to measure - 3b boom unable to reach area due to machine limitations | [7 empty] | N/A
[7 empty] | 25 |  |  |  |  | 27
[7 empty] | 26 |  |  |  |  | 28 | missing
Weather:
12oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 |  | SLM cal expiry: 23/05/2026 |  | Cert: UCRT24/1777
Wind: up to 1.3ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 |  | Cal cal expiry: 29/07/2026 |  | Cert: CE-REP-10992

## Main Building - Roof
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
Main Building - Roof | DX Cooling unit (East) | 29 | L646 | 26/03/2026 | 13:57 | 1 minute | 66.54 | 54.57 | 55.6 | 52.2 | Noise source dominant - x24 on roof, only one measured as only a couple running |  |  |  | Unable to access north and south side |  |  | Daikin Sky Air R32 Alpha | Engineer informed me that the roof plant items are designed to be run at a whisper due to sensitive internal conditions. Additionally, not all roof plant items are running as only one pharmaceutical production lane is ready to go into operation. The plan eventually is to have 5 production lanes open and the plant items reqiuired to support this are already in place.
| DX Cooling unit (West) | 30 | L647 | 26/03/2026 | 13:59 | 1 minute | 61.48 | 54.01 | 56 | 51.2 | Noise source dominant - x24 on roof, only one measured as only a couple running
| Penthouse louvre - HVAC exhaust (east) | 31 | L648 | 26/03/2026 | 14:01 | 1 minute | 64.78 | 59.66 | 60.3 | 59 | Noise source dominant - x14 on roof, only one measured as not all running |  |  |  | Subjectively the noisiest plant item on the roof |  |  | Various
| Penthouse louvre - HVAC exhaust (west) | 32 | L649 | 26/03/2026 | 14:03 | 1 minute | 73.63 | 57.5 | 57.9 | 56 | Noise source dominant - x14 on roof, only one measured as not all running
| Penthouse louvre - HVAC exhaust (north) | 33 | L650 | 26/03/2026 | 14:04 | 1 minute | 67.5 | 62.8 | 63.7 | 62 | Noise source dominant - x14 on roof, only one measured as not all running
| Penthouse louvre - HVAC exhaust (south) | 34 | L651 | 26/03/2026 | 14:12 | 1 minute | 76.48 | 57.34 | 56.9 | 48.1 | Noise source dominant - x14 on roof, only one measured as not all running
| CO2 cold room cooling unit (east) | 35 | L652 | 26/03/2026 | 14:13 | 1 minute | 71.83 | 55.3 | 56.3 | 48.1 | Noise source dominant - nearby RTN also noted - x4 on roof, only one measured |  |  |  | West side - No noise audible, RTN dominant |  |  | Panasonic R744
| CO2 cold room cooling unit (south) | 36 | L653 | 26/03/2026 | 14:15 | 1 minute | 68.33 | 55.2 | 56.7 | 49.6 | Noise source dominant - nearby RTN also noted - x4 on roof, only one measured
| CO2 cold room cooling unit (north) | 37 | L654 | 26/03/2026 | 14:17 | 1 minute | 67.08 | 52.34 | 52.3 | 48.1 | Noise source dominant - nearby RTN also noted - x4 on roof, only one measured
| DX cooling to data centre | 38 | Not running due to current operational building condition - x2 on roof | [7 empty] | Same size, make and model as Plant no. 29/30 - Daikin Sky Air R32 Alpha
| PV Panel inverters | 39 | Not running due to current operational building condition - x4 on roof
| Nitrogen safety valve exhaust | 40 | Not measured, no noise audible. RTN dominant from 1m away
| VHP - HVAC exhaust | 41
| WFI relief vent | 42 | Not measured, no noise audible. Just open vents to air - RTN dominant from 1m away
| Process waste vent | 43
[7 empty] | 29&30 |  |  |  |  | 33 |  | 36 |  | 36
[7 empty] | 31 |  |  |  |  | 34 |  | 37 |  | 37
[7 empty] | 32 |  |  |  |  | 35 |  |  |  | 38 | Missing
39
40
41
42 & 43
Weather:
[8 empty] | 12oC, sunny, clear, dry |  |  | SLM | Svantek 971 - SN: 111622 | SLM cal expiry: 23/05/2026 | Cert: UCRT24/1777
[8 empty] | Wind: up to 1.9ms in places |  |  | Calibrator | Rion NC-75 - SN: 34391438 | Cal cal expiry: 29/07/2026 | Cert: CE-REP-10992

## West Facade
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
West Façade | HVAC fresh air intake louvre (1 intake) | 44 | L655 | 26/03/2026 | 14:25 | 1 minute | 68.98 | 63.85 | 65.6 | 54 | Measured from inside intake room - Plant running but RTN from Cowpen Lane also audible |  |  | No access to external west façade for 3b boom
| HVAC fresh air intake louvres (2 intakes) | 45 | L658 | 26/03/2026 | 14:30 | 1 minute | 64.52 | 60.85 | 63 | 56.9 | Measured from inside intake room - Plant running but RTN from Cowpen Lane also audible
44
[10 empty] | 45 | Missing
[11 empty] | SLM | Svantek 971 - SN: 111622 | SLM cal expiry: 23/05/2026 | Cert: UCRT24/1777
[11 empty] | Calibrator | Rion NC-75 - SN: 34391438 | Cal cal expiry: 29/07/2026 | Cert: CE-REP-10992

## L1 Roof
Measurements across site |  | All measurements 1 metre from source or weakest facade area (doors / shutters / windows / louvres etc) unless otherwise stated
Area | Item | No. | ID | Date | Time | Duration | LAFmax | LAeq | L10 | L90 | Notes / DNS
L1 Roof | DX cooling unit for comms room (east) | 46 | L659 | 26/03/2026 | 14:35 | 1 minute | 64.9 | 54.18 | 56.8 | 49.1 | DX unit running at a whisper due to site conditions - noise source dom but some intermittent site noise audible |  | Unable to measure at rear of units (west) | 659 : Total results
| DX cooling unit to L1 cold room (east) | 47 | L660 | 26/03/2026 | 14:37 | 1 minute | 64.25 | 51.63 | 54.8 | 45.2 | Only one unit running - noise source dom but some intermittent site noise audible
| Air source heat pumps & chiller (south) | 48 | L662 | 26/03/2026 | 14:46 | 1 minute | 62.84 | 50.94 | 52.3 | 48.4 | Only one live unit running - source dominant - unable to measure at west location | [6 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
| Air source heat pumps & chiller (north) | 49 | L663 | 26/03/2026 | 14:47 | 1 minute | 62.23 | 54.68 | 57.3 | 50.3 | [7 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
| Air source heat pumps & chiller (east) | 50 | L664 | 26/03/2026 | 14:49 | 1 minute | 64.66 | 50.73 | 52 | 47.7 |  |  |  | No. | Start date & time | Duration | Name |  |  | L10 | L90
[14 empty] | 1 | 26/03/2026 14:35:28.000 | 00:01:00.000 | Integration period 1 m | 64.9 | 54.18 | 56.8 | 49.1
[10 empty] | 46 |  | 49
660 : Total results
[18 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
[18 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
[14 empty] | No. | Start date & time | Duration | Name |  |  | L10 | L90
[14 empty] | 1 | 26/03/2026 14:37:42.000 | 00:01:00.000 | Integration period 1 m | 64.25 | 51.63 | 54.8 | 45.2
[10 empty] | 47 |  | 50
662 : Total results
[18 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
[18 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
[14 empty] | No. | Start date & time | Duration | Name |  |  | L10 | L90
[14 empty] | 1 | 26/03/2026 14:46:30.000 | 00:01:00.000 | Integration period 1 m | 62.84 | 50.94 | 52.3 | 48.4
663 : Total results
[18 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
[10 empty] | 48 | [7 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
[14 empty] | No. | Start date & time | Duration | Name |  |  | L10 | L90
[14 empty] | 1 | 26/03/2026 14:47:52.000 | 00:01:00.000 | Integration period 1 m | 62.23 | 54.68 | 57.3 | 50.3
664 : Total results
[18 empty] | P1 (A, Fast) | P1 (A, Lin) | P1 (A, Lin) | P1 (A, Lin)
[18 empty] | LAFmax (SR) [dB] | LAeq (SR) [dB] | LAeq Histogram (SR) [dB] | LAeq Histogram (SR) [dB]
[14 empty] | No. | Start date & time | Duration | Name |  |  | L10 | L90
[14 empty] | 1 | 26/03/2026 14:49:22.000 | 00:01:00.000 | Integration period 1 m | 64.66 | 50.73 | 52 | 47.7
11oC, sunny, clear, dry | SLM | Svantek 971 - SN: 111622 |  |  | SLM cal expiry: 23/05/2026 |  |  | Cert: UCRT24/1777
Wind: up to 1.1ms in places | Calibrator | Rion NC-75 - SN: 34391438 |  |  | Cal cal expiry: 29/07/2026 |  |  | Cert: CE-REP-10992