Technical Standards

Storage

Tank Construction Testing Certification & Listing:

BS-EN 12285 – 2 : 2005

4 Hour Fire Rating

SwRI Standard 95-03 and 93-01

UFC A-II-F-1

UL2085

Monitoring & Gauging:

Directive 94/9/EC

EN 60079-0 : 2006

EN 60079-11 : 2007

EN 60079-26 : 2007

Directive 2004/108/EC (EMC)

EN 61000-6-2 :2005

EN 61000-6-3 :2007

ATEX

The Refuels Ltd Supervault MH Tanks have the following systems in line with UL2085 (US) & KIWA (EU) requirements:

- HLCO High level cut-off alarm system.

- Real time tank content volume and temperature monitoring.

- Dry brake user couplings.

- Vapour recovery integral for uplifting operations.

- User specific security and access control.

- Integral self bunding.

- Earth circuit continuity.

- PPV Pressure proportioning.

- Frangible disc explosion protection.

They are also subject to Type Approval consisting of testing against those standards as below:

- 4-Hour, 2000º F Fire Test, Internal temperature increased only 165º F

- Immediately after the Fire Test the hot tank is exposed to a Hose Stream Test

- The same tank is shot with 5 rounds of 150 grain M-2 ball ammunition (823m/sec.) The bullets penetrate the outer containment tank and stop in the insulation.

- Finally the same tank is exposed to another two hour fire test with the same pass/fail criteria of the first.

General Site Requirements

- Tank size – 7.8 metres length, 2.1 metres height & 1.8 metres width.

- Hard standing for tank and vehicle operations.

- Intercepted, contained or groundwater secured vehicle operations area.

- Security lighting.

- Security controlled – gated or monitored.

- Appropriate access / egress.

Transportation

European Agreement Concerning the Carriage of Dangerous Goods By Road (ADR 2025)

The Carriage of Dangerous Goods by Road Regulations 2009 (As Amended)

Commissioning/Decommissioning of Sites

Guidance for Design, Construction, Modification, Maintenance and Decommissioning of Filling Stations (Blue Book 5th Edition)