## Info
Operator: | Northumbrian Water
Permit Ref: | EPR/KP3394ZE
Site: | Howdon Sludge Treatment Centre (STC)
Date: | 2023-02-24
Full Waste Treatment BREF
Waste Treatment BAT Conclusions
This document has been compiled as a tool to help clearly identify where there may be gaps in complying with the Waste Treatment BAT conclusions. The information contained only relates to:
General BAT conclusions
General BAT conclusions for the biological treatment of waste
BAT conclusions for the aerobic treatment of waste
BAT conclusions for the anaerobic treatment of waste
BAT conclusions for the mechanical biological treatment (MBT) of waste
BAT conclusions for the physico-chemical treatment of solid and/or pasty waste
Additional BAT conclusions may apply depending on the operations carried out.
It can be used by applicants/operators or EA officers but is not a substitution for the official BAT documents or other official Environment Agency guidance.

## BAT Conclusions
BAT No. | Topic | Brief Description | BAT | Applicable BAT- AEL | Compliant now? | Derogation needed? | Provide brief comments on how compliance with BAT is (or will be) achieved Where "N/A" or "other" is given, please explain why
General BAT conclusions
1 | Overall performance | EMS Applicability The scope (e.g. level of detail) and nature of the EMS (e.g. standardised or non-standardised) will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed). | In order to improve the overall environmental performance, BAT is to implement and adhere to an environmental management system (EMS) that incorporates all of the following features:
|  |  | i) commitment of the management, including senior management; |  | Yes |  | IS014001
|  |  | ii) definition, by the management, of an environmental policy that includes the continuous improvement of the environmental performance of the installation; |  | Yes |  | IS014001
|  |  | iii) planning and establishing the necessary procedures, objectives and targets, in conjunction with financial planning and investment; |  | Yes |  | IS014001
|  |  | iv) implementation of procedures paying particular attention to: (a) structure and responsibility, (b) recruitment, training, awareness and competence (c) communication, (d) employee involvement, (e) documentation, (f) effective process control, (g) maintenance programmes, (h) emergency preparedness and response, (i) safeguarding compliance with environmental legislation; |  | Yes |  | IS014001
|  |  | v) checking performance and taking corrective action, paying particular attention to: (a) monitoring and measurement (see also the JRC Reference Report on Monitoring of emissions to air and water from IED installations – ROM), (b) corrective and preventive action, (c) maintenance of records, (d) independent (where practicable) internal or external auditing in order to determine whether or not the EMS conforms to planned arrangements and has been properly implemented and maintained; |  | Yes |  | Daily, monthly, quarterly, six monthly and annual monitoring and measurement
|  |  | vi) review, by senior management, of the EMS and its continuing suitability, adequacy and effectiveness; |  | Yes |  | Monthly Senior Management reviews of compliance, efficiency and performance. Actions agreed/implemented.
|  |  | vii) following the development of cleaner technologies; |  | Yes |  | R&D constantly looking at emerging technologies and innovative methods for sludge treatment e.g. solar power, hydro generation, ionisation of odour emissions, DNA profiling of digestion process, THP/BAS/End of Waste, algae treatment of ammonia liquors, digestate degassing, sonification....
|  |  | viii) consideration for the environmental impacts from the eventual decommissioning of the plant at the stage of designing a new plant, and throughout its operating life; |  | Yes |  | Site Condition plan 2011, updated for permit variation in 2022.
|  |  | ix) application of sectoral benchmarking on a regular basis; |  | Yes |  | Set of KPIs used and reported daily on Advanced Anaerobic Digestion (AAD). Daily and weekly reports. Comparison of process performance across water sector.
|  |  | x) waste stream management (see BAT 2); |  | Yes |  | Continuous, daily sampling of % dry solids of incoming NWL sludges
|  |  | xi) an inventory of waste water and waste gas streams (see BAT 3); |  | To be implemented |  | See BAT 3 for further comment
|  |  | xii) residues management plan (see description in Section 6.5); |  | Yes |  | Residues for AD activities include digestate and liquors a.k.a. by-products and wastes generated from the treatment of sludge. Residues Management Plan is part of the EMS and is reviewed to ensure compliance with BAT. Resultant Digestate is a useful product as an agricultural fertilizer. Odours are captured and returned to process for treatment.
|  |  | xiii) accident management plan (see description in Section 6.5); |  | Yes |  | Company and Site Specific Emergency plan with additional local resources available (as well as normal emergency services). The Site operates under a site-specific Accident Management Plan, referred to by Northumbrian Water as the Site Emergency Incident Plan, to prevent and manage environmental related accidents. The site-specific AMP includes a description of emergency response procedures, management of accidental emissions (such as spills) and registration and assessment of accidents.
2 | Overall performance | Improvement of overall environmental performance | In order to improve the overall environmental performance of the plant, BAT is to use all of the techniques given below. |  |  |  | Continuous and daily analysis for %DS but will need characterization of incoming sludges. See sections below for further comment on compliance with BAT 2.
|  |  | a) Set up and implement waste characterisation and pre-acceptance procedures |  | To be implemented |  | This is ongoing with plans to commence sampling in June 2023. The finalised procedures will be completed within 12months of the commencement of sampling to ensure sludge characterisation is appropriately undertaken using the sampling data.
|  |  | b) Set up and implement waste acceptance procedures |  | To be implemented |  | Finalised procedures to be completed no later than July 2023. Latest version of the procedure is 100105164_BAT_WasteAcceptance_HOW
|  |  | c) Set up and implement a waste tracking system and inventory |  | Yes |  | Gemini and GPS load tracking. JRP system monitoring and reporting all loads. Backed up with weighbridge procedures and telematics.
|  |  | d) Set up and implement an output quality management system |  | Yes |  | HACCP/BAS compliant with output sampling and analysis.
|  |  | e) Ensure waste segregation |  | Yes |  | Currently the Site accepts indigenous sludge and imported liquid sludge. Cake is imported on occasion. Sludge that is delivered to the Site is transported in tankers. Indigenous sludge is forwarded to a pre-dewatering and screening facility where it passes through 6 No. strain presses. It is then temporarily stored in a screened sludge buffer tank prior to being passed through 2 No. centrifuges. Digested sludge is stored in 1 No. post digestion sludge storage tank before being dewatered by 2 No. centrifuges in the dewatering treatment plant, after which it is transferred by screw conveyor to a sludge cake silo.
|  |  | f) Ensure waste compatibility prior to mixing or blending of waste |  | Yes |  | The wastes accepted has a very low risk of non-compatibility with any other waste or substances that are, or could, be present on site which could cause gas evolution, precipitation etc. At larger and coastal sites, operators take sludge samples for total solids and would use experience to note any irregularities by sight/odour. At smaller sites, de-sludging is carried out manually so again, operator experience would be used to determine any issues. Characterisation of incoming sludge as in 2 (a). Primary, secondary and imported sludge is combined in strategic storage tanks which have compressed air forced in to mix with extraction to an OCU. Wessoe valves allow a specific number of air changes. Any issues with sludge would be noticed. No incident of this nature has ever occured.
|  |  | g) Sort incoming solid waste |  | Yes |  | All sludge is screened after being received so if there are an unwanted material in the imports then this will be removed through this process.
3 | Overall performance | Inventory Applicability The scope (e.g. level of detail) and nature of the inventory will generally be related to the nature, scale and complexity of the installation, and the range of environmental impacts it may have (determined also by the type and amount of wastes processed). | In order to facilitate the reduction of emissions to water and air, BAT is to establish and to maintain an inventory of waste water and waste gas streams, as part of the environmental management system (see BAT 1), that incorporates all of the following features:
|  |  | (i) information about the characteristics of the waste to be treated and the waste treatment processes, including: (a) simplified process flow sheets that show the origin of the emissions; (b) descriptions of process-integrated techniques and waste water/waste gas treatment at source including their performances; |  | Yes |  | Fully documented. Mass/Energy balance. Process Flow Diagrams. Sampling and analysis plan to be developed and implemented by January 2023.
|  |  | (ii) information about the characteristics of the waste water streams, such as: (a) average values and variability of flow, pH, temperature, and conductivity; (b) average concentration and load values of relevant substances and their variability (e.g. COD/TOC, nitrogen species, phosphorus, metals, priority substances/micropollutants); (c) data on bioeliminability (e.g. BOD, BOD to COD ratio, Zahn-Wellens test, biological inhibition potential (e.g. inhibition of activated sludge)) (see BAT 52); |  | Yes |  | Waste streams fully documented and controlled: blowdown, surface water from process areas, raw centrate, digested centrate, biofilter effluent. Flows measured, sampled and analysed for BOD, COD, pH, ammonia and suspended solids. NWL are committed to undertaking the sampling and analysis in line with BAT 3, see Part C6 applicaiton form and Section 7 of the Main Supporting Document.
|  |  | (iii) information about the characteristics of the waste gas streams, such as: (a) average values and variability of flow and temperature; (b) average concentration and load values of relevant substances and their variability (e.g. organic compounds, POPs such as PCBs); (c) flammability, lower and higher explosive limits, reactivity; (d) presence of other substances that may affect the waste gas treatment system or plant safety (e.g. oxygen, nitrogen, water vapour, dust). |  | Yes |  | Process streams fully documented and controlled: Biogas, biomethane, Off Gas from Biomethane Upgrade and foul gas from THP process. Flows measured and content monitored.
4 | Overall performance | Techniques for storage of waste | In order to reduce the environmental risk associated with the storage of waste, BAT is to use all of the techniques given below.
|  |  | a) Optimised storage location |  | Yes |  | NWL Sludge Strategy covers source STWs delivering "fresh sludge" to two main STPs either directly of via six satellite dewatering facilities. "Fresh Sludge" produces more biogas. Excessive upstream storage results in loss of sludge value i.e. cold digestion occurring. The storage location is along the southern permit boundary of the site. The sludge is proposed to be stored here as this is the natural flow path for the sludge and still maintains access in, out and within the site. The storage location is also in close proximity to the sludge storage tanks on the southern boundary, which could be used in emergencies if an alternative tank failed. All drainage on the site is treated; any pipes which discharge from the site into the watercourse will be fitted with an automated penstock, which will be able to be closed to minimise the spill to the river. The tanks are situated centrally on the site so as to be as far from the river as possible whilst also protecting the local population from any odours emanating from tankering discharge or the tanks themselves.
|  |  | b) Adequate storage capacity |  | Yes |  | Buffer capacity for process variation is NWL philosophy. Review underway to look at increasing the latter for raw sludge imports. Weekly planning and review meeting between Howdon Ops and Bioresources Team - decision on imported amounts from whcih sites. Maintenance issues discussed and mitigation measures put in place in case of problems. Strategic storage tanks have independent level monitors and monitoed via SCADA and MIPS. Daily sludge productivity graphs are generated via MIPS and issued automatically at 6 a.m. every day to Ops, Bioresources and Compliance Teams.
|  |  | c) Safe storage operation |  | Yes |  | Loading and unloading equipment clearly documented/labelled with security devices.
|  |  | d) Separate area for storage and handling of packaged hazardous waste |  | N/A (explain) |  | No hazardous waste accepted/treated.
5 | Overall performance | Techniques for handling and transfer of waste | In order to reduce the environmental risk associated with the handling and transfer of waste, BAT is to set up and implement handling and transfer procedures. |  | Yes |  | Trained staff (training matrix, NVQ…), JRP/Gemini/Weighbridge facilities utilised. Appropriate equipment trials undertaken before implementation. All projects undertake HAZOPs looking at safe receipt, mixing, blending, processing and despatch.
6 | Monitoring | Waste water - Monitor key parameters | For relevant emissions to water as identified by the inventory of waste water streams (see BAT 3), BAT is to monitor key process parameters (e.g. waste water flow, pH, temperature, conductivity, BOD) at key locations (e.g. at the inlet and/or outlet of the pretreatment, at the inlet to the final treatment, at the point where the emission leaves the installation). |  | To be implemented |  | Parameters for liquor sampling: Effluent liquors (“returned liquors”) from STCs are pumped to the site’s HoW and are treated alongside the crude sewage influent in the WwTW. The sampling would ideally include the parameters in the table below. CRUDE LIQUOR RETURN Ammonia Ammonia Settled BOD Settled BOD COD COD Total Solids Total Solids PFOS PFOA Total Nitrogen Total Organic Carbon Total Phosphate Procurement of services for sampling, or implementation for in-house sampling, is scheduled to begin no later than June 2023
7 | Monitoring | Waste water - Monitoring frequencies and standards | BAT is to monitor emissions to water with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality. | See 'Water emissions tables' tab | To be implemented |  | See BAT 6 for the parameters to be measured for waste waters. Procurement of services for sampling, or implementation for in-house sampling, is scheduled to begin no later than June 2023
8 | Monitoring | Channelled air emissions - Monitoring frequencies and standards | BAT is to monitor channelled emissions to air with at least the frequency given below, and in accordance with EN standards. If EN standards are not available, BAT is to use ISO, national or other international standards that ensure the provision of data of an equivalent scientific quality. | See 'Air emissions tables' tab | Yes |  | H2S +NH3 or odour conc every 6 months
9 | Monitoring | Diffuse emissions - Monitor organic compounds | BAT is to monitor diffuse emissions of organic compounds to air from the regeneration of spent solvents, the decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery of their calorific value, at least once per year using one or a combination of the techniques given below. |  | N/A (explain) |  | No regeneration of spent solvents, decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery
|  |  | a) Measurement |  | N/A (explain) |  | No regeneration of spent solvents, decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery
|  |  | b) Emissions factors |  | N/A (explain) |  | No regeneration of spent solvents, decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery
|  |  | c) Mass balance |  | N/A (explain) |  | No regeneration of spent solvents, decontamination of equipment containing POPs with solvents, and the physico-chemical treatment of solvents for the recovery
10 | Monitoring | Odour - Monitor emissions Applicability The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | BAT is to periodically monitor odour emissions. (The monitoring frequency is determined in the odour management plan (see BAT 12).) |  | Yes |  | Addressed in the OMP, in particular Section 'Odour Monitoring System'.
11 | Monitoring | Monitor annual consumption and generation of waste outputs | BAT is to monitor the annual consumption of water, energy and raw materials as well as the annual generation of residues and waste water, with a frequency of at least once per year. |  | Yes |  | Meters are on site to allow for monitoring on issue of a permit.
12 | Emissions to air | Odour Management Plan Applicability The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to set up, implement and regularly review an odour management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements: — a protocol containing actions and timelines; — a protocol for conducting odour monitoring as set out in BAT 10; — a protocol for response to identified odour incidents, e.g. complaints; —an odour prevention and reduction programme designed to identify the source(s); to characterise the contributions of the sources; and to implement prevention and/or reduction measures. |  | Yes |  | OMP has been provided in the application with consideration to the BAT conclusions and Environment Agency H4 guidance.
13 | Emissions to air | Odour reduction techniques | In order to prevent or, where that is not practicable, to reduce odour emissions, BAT is to use one or a combination of the techniques given below.
|  |  | a) Minimising residence times |  | N/A (explain) |  | BAT applies to open systems. Key operations take place within a closed system, including covered tanks, pipework and machinery. The anaerobic digestion vessels are sealed and biogas is extracted from the vessels.
|  |  | b) Using chemical treatment |  | N/A (explain) |  | Current treatment is biofilter, carbon filter and ventri condenser.
|  |  | c) Optimising aerobic treatment |  | N/A (explain) |  | It is an anaerobic sludge treatment process.
14 | Emissions to air | Diffuse emission reduction techniques | In order to prevent or, where that is not practicable, to reduce diffuse emissions to air, in particular of dust, organic compounds and odour, BAT is to use an appropriate combination of the techniques given below. Depending on the risk posed by the waste in terms of diffuse emissions to air, BAT 14d is especially relevant.
|  |  | a) Minimising the number of potential diffuse emission sources |  | Yes |  | Included in process design. For e.g. pipe work specifications, drop height restrictions, installation of wind barriers etc. NWL work to internal engineering standard specifications whcih reference British Standards. These documents are reviewed in line with quality procedures so as to be up to date. Gravity transfer is used where possible. Traffic speed is limited to 10 mph on site by used of signs and sleeping policeman.
|  |  | b) Selection and use of high- integrity equipment |  | Yes |  | Included in process design. NWL policy is to use high-integrity equipment such as: — valves with double packing seals or equally efficient equipment; — high-integrity gaskets (such as spiral wound, ring joints) for critical applications; — pumps/compressors/agitators fitted with mechanical seals instead of packing; — magnetically driven pumps/compressors/agitators. NWL work to internal engineering standard specifications which reference British Standards. These documents are reviewed in line with quality procedures so as to be up to date.
|  |  | c) Corrosion prevention |  | Yes |  | Included in process design. NWL work to internal engineering standard specifications whcih reference British Standards and Water Industry Mechanical & Electrical Specifications (WIMES). These documents are reviewed in line with quality procedures so as to be up to date. Or to European standards where applicable, depending where equipment is made.
|  |  | d) Containment, collection and treatment of diffuse emissions |  | Yes |  | Included in process design. Key operations take place within a closed system, including covered tanks, pipework and machinery. The anaerobic digestion vessels are sealed and biogas is extracted from the vessels. a) The monitoring of gas production rates to prevent excess pressure in storage tanks and vessels is carried out via SCADA and CAMBI is then set up to match output b) Pressure Release Valves PRVs are designed to British Standards. c). Bursting discs, Whessoe valves are used in the digestion process and storage vessels. Contract with UTILE for annual inspections and instrumentation checks. PRVs are removed and sent to accredited facility for inspection and re-calibration. d) NWL restricts using pressure relief valves so they activate in emergency situations only. Priority 2 Alarms lead to an immediate Operations response. e) To log and record release events from PRVs; SCADA high high alarms but as these sometimes alarm in e.g. high wind, they are also validated by analysis of the amounts of gas passing into the system. f) Please confirm the location of all PRVs as these will need to be added to the site plan (The plan currently includes those on the digestors, gas holder, boilers) In addition, PRVs on sludge feed, rising main (high = blockage, low = other issue) BUP + grid entry unit - insurance inspection with written scheme of examination 2 years for PRV/vessel. Columns 5 years - internal welds and integrity check. PRVs removed and sent to accredited facility for recalibration and certification.
|  |  | e) Dampening |  | Yes |  | The process does not give rise to diffuse dust emissions. In periods of dry weather, traffic areas are cleaned by water tanker.
|  |  | f) Maintenance |  | Yes |  | Maximo used to control ppms and reactive maintenance.
|  |  | g) Cleaning of waste treatment and storage areas |  | Yes |  | Operations undertake regular cleaning/washing down of process areas/minor spillages to minimise odour emissions.
|  |  | h) Leak detection and repair (LDAR) programme |  | To be implemented |  | Operations utilise a combination of SCADA monitoring/alarms/daily walkarounds/occasional leak detection (leak detection & CCTV). A LDAR Plan is in development in accordance with the Environment Agency Appropriate Measures for Biological Waste, and currently under going review. It will be available for issue no later than 30th June 2023
15 | Emissions to air | Flare use minisation techniques | BAT is to use flaring only for safety reasons or for non-routine operating conditions (e.g. start-ups, shutdowns) by using both of the techniques given below.
|  |  | a) correct plant design |  | Yes |  | Design philosophy is to minimise flaring. The latter is constantly reviewed post installation and already reported to EA as per permit.
|  |  | b) Plant management |  | Yes |  | As above. Regular servicing carried out. Software modifications carried out to reduce flaring. New project review underway to recover reject gas and further reduce flaring.
16 | Emissions to air | Flare emissions minisation techniques | In order to reduce emissions to air from flares when flaring is unavoidable, BAT is to use both of the techniques given below.
|  |  | a) Correct design of flaring devices |  | Yes |  | Uniflare UFO-3500-ENV installed January 2012 complies with EC directives as applicable and used in accordance with 'Monitoring enclosed landfill gas flares: LFTGN05'
|  |  | b) Monitoring and recording as part of flare management |  | Yes |  | No. of hours are recorded in SCADA. Triggers in place because any issue causing flaring is sorted ASAP as potential loss of revenue.
17 | Noise and vibrations | Noise management plan Applicability The applicability is restricted to cases where a noise or vibration nuisance at sensitive receptors is expected and/or has been substantiated. | In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to set up, implement and regularly review a noise and vibration management plan, as part of the environmental management system (see BAT 1), that includes all of the following elements: |  | N/A (explain) |  | Based on the 'applicability' criteria stated in the BAT Conclusions, the site is not applicable for requiring a NMP. The site does not generate levels of noise and vibration to be considered a nuisance or risk to sensitive receptors, the site has not had substantiated concerns raised. The Site does have a Noise Management Plan 'NWL Document: HSM 02.18 Noise Management'.
|  |  | i) a protocol containing appropriate actions and timelines; |  | N/A (explain) |  | As above
|  |  | ii) a protocol for conducting noise and vibration monitoring; |  | N/A (explain) |  | As above
|  |  | iii) a protocol for response to identified noise and vibration events, e.g. complaints; |  | N/A (explain) |  | As above
|  |  | iv) a noise and vibration reduction programme designed to identify the source(s), to measure/estimate noise and vibration exposure, to characterise the contributions of the sources and to implement prevention and/or reduction measures. |  | N/A (explain) |  | As above
18 | Noise and vibrations | Noise and vibration reduction techniques | In order to prevent or, where that is not practicable, to reduce noise and vibration emissions, BAT is to use one or a combination of the techniques given below.
|  |  | a) Appropriate location of equipment and buildings |  | Yes |  | For noise and vibration - Original specification for Cambi sludge treatment plant required piping systems and connections to be properly anchored and supported to BS and/or European standard. Noise reports and vibration reports carried out during site commissioning. Low noise equipment utlilised where possible. Noise surveys carried out. Buildings also block the noise from workplaces on site and from local housing. There are also earth bunds/trees between the site and the local population.
|  |  | b) Operational measures |  | Yes |  | Inspection and maintenance of equipment carried out according to EMS. Doors are kept closed whenever possible. Tankering does occur 24 hours a day but NWL operates a complaint procedure via 24 hours reception centre.
|  |  | c) Low-noise equipment |  | Yes |  | Low noise equipment used where possible.
|  |  | d) Noise and vibration control equipment |  | Yes |  | Operations carried out indoors where possible. Soundproofing of buildings carried out.
|  |  | e) noise attenuation |  | Yes |  | Earth bunds/embankments and trees between site and local population.
19 | Emissions to water | Water management techniques | In order to optimise water consumption, to reduce the volume of waste water generated and to prevent or, where that is not practicable, to reduce emissions to soil and water, BAT is to use an appropriate combination of the techniques given below.
|  |  | a) water management |  | Yes |  | Flow measurement and review of consumption reported to EA. Example of water usage reduction: Water softening followed by reverse osmosis to reduce blow down thereby energy/water wastage.
|  |  | b) water recirculation |  | Yes |  | Reuse of final effluent where appropriate.
|  |  | c) impermeable surface |  | Yes |  | The surface of the whole waste treatment area (e.g. waste reception, handling, storage, treatment and dispatch areas) is impermeable.
|  |  | d) Techniques to reduce the likelihood and impact of overflows and failures from tanks and vessels |  | Yes |  | Multi number/type of Level monitoring, process interlocks, tank inspections (external & internal), bunding philosophy, drain cleaning…. All tanks have level sensors that are operational at all times to understand the level of sludge in each tank. The process stream can be adjusted accordingly, reducing the treatment capacity of the treatment works if these tanks trigger the overflow alarms. There are also storm tanks on site where sewage can be stored prior to first treatment if necessary if there is an operational issue further through the treatment stream. Both sites are manned 24/7, so any issues can be dealt which quickly and efficiently. All tanks are subject to a regular maintenance regime to assess the risk of any failures or non operational valves. The topography of the land is such that all site drainage flows south and/or south west towards the River Tyne. The proposed option which will be refined during the detailed design stage will retain all sludge flows within the south and south west boundary, and a flood gate will be installed on the eastern side on the access road to retain all sludge within the site boundary. Access in and out of the site has been maintained. Any permeable areas will be lined to reduce the risk of sludge entering the groundwater store through infiltration. Any site drainage that discharges into a watercourse or ditch and does not return to the treatment process will have an automated flap valve installed which can be closed in an event of a spill, minimising the impact to the environment where possible. Proposed design solutions set out in the FA05-01a-NWG-IED-HOWD-001 - IED Risk Register-Howdon v2 identify adequate storage and buffer capacity. Detailed design, (currently in discussion with NWL of this), will refine the secondary containment needs further and may identify more appropriate isolated containment measures.
|  |  | e) Roofing of waste storage and treatment areas |  | Yes |  | All storage tanks are covered or enclosed. Cake is stored in a silo and remains covered during transportation.
|  |  | f) Segregation of water streams |  | Yes |  | Raw water, final effluent, high quality process water and potable are segregated to avoid inappropriate contamination (Compliance with Water Byelaws).
|  |  | g) Adequate drainage infrastructure |  | Yes |  | All storage tanks are covered or enclosed. Cake is stored in a silo and remains covered during transportation. Wastes are not exposed to rainwater.
|  |  | h) Design and maintenance provisions to allow detection and repair of leaks |  | Yes |  | Further procedures to be implemented as per BAT 14h
|  |  | i) Appropriate buffer storage capacity |  | Yes |  | Proposed design solutions set out in the FA05-01a-NWG-IED-HOWD-001 - IED Risk Register-Howdon v2 identify adequate storage and buffer capacity. Detailed design stage will likely refine proposed designs.
20 | Emissions to water | Water emission reduction techniques | In order to reduce emissions to water, BAT is to treat waste water using an appropriate combination of the techniques given below. | See 'Water emissions tables' tab | To be implemented |  | Waste water is routed to the head of the works to be treated through the wastewater treatment works, regulated under Urban Wastewater Treatment Regulations. The only indirect emission is of the sludge liquors and surface waters, which are returned to the wastewater treatment works for aerobic treatment under Urban Wastewater regulations. The liquors returned from the sludge treatment facility have originated from wastewater treatment works that are also under the control of NWL. Therefore the majority of process controls and sampling are carried out upstream of the point where liquors are returned from the sludge treatment facility to the onsite wastewater treatment works. NWL currently samples pH, Ammonium, BOD, COD and Suspended Solids on the centrate return liquor. NWL are costing the additional determinands. Direct regular sampling of these returns is a new requirement for our processes so our understanding of the variance in these returns will develop with time. NWL will carry out root cause investigations with the process support teams to understand what is present and ensure that we can reduce the risk to the inlet. If any abnormalities are identified in the sample data, the team will be instructed to increase catchment sampling to ascertain the cause. PFOS and PFOA will be added to the sample regime when an accredited method is available. However, it is unlikely that this analysis would be carried out under a 10 day turnround time, meaning it would not be possible to react in a sufficient timescale to find a root cause. Inlet monitoring is also required, to ensure that any substances present in the returns at elevated concentrations, can be addressed as to whether they are present in the incoming effluent or are a product of the installation activities. The STC discharges into the primary distribution chamber (post inlet works). A flow monitoring point may be required for the discharges from the installation to the effluent discharge point (AB on the site layout plan) (its final location and confirmation it meets MCERTS is included in the application form). NWL are currently progressing design and identifying location and requirement for the installation of flow monitoring. All required flow monitoring will be installed by end April 2024.
|  |  | a) equalisation |  | N/A (explain)
|  |  | b) neutralisation |  | N/A (explain)
|  |  | c) Physical separation, e.g. screens, sieves, grit separators, grease separators, oil- water separation or primary settlement tanks |  | Yes |  | The site has a Preliminary Treatment Area. The screenings handling plant and the associated screen hall, conveyors and skips are all enclosed in a single building. The grit removal system is also enclosed within a building and the treatment unit is covered
|  |  | d) adsorption |  | N/A (explain)
|  |  | e) distillation/rectification |  | N/A (explain)
|  |  | f) precipitation |  | N/A (explain)
|  |  | g) chemical oxidation |  | N/A (explain)
|  |  | h) chemical reduction |  | N/A (explain)
|  |  | i) evaporation |  | N/A (explain)
|  |  | j) ion exchange |  | N/A (explain)
|  |  | k) stripping |  | N/A (explain)
|  |  | l) activated sludge process |  | N/A (explain)
|  |  | m) membrane bioreactor |  | N/A (explain)
|  |  | n) Nitrification/denitrification when the treatment includes a biological treatment |  | N/A (explain)
|  |  | o) coagulation and flocculation |  | N/A (explain)
|  |  | p) sedimentation |  | N/A (explain)
|  |  | q) Filtration (e.g. sand filtration, microfiltration, ultrafiltration) |  | N/A (explain)
|  |  | r) floatation |  | N/A (explain)
21 | Emissions from accidents and incidents | Prevention and limitation techniques | In order to prevent or limit the environmental consequences of accidents and incidents, BAT is to use all of the techniques given below, as part of the accident management plan (see BAT 1). |  |  |  | The Site operates under a site-specific Accident Management Plan, referred to by Northumbrian Water as the Site Emergency Incident Plan, to prevent and manage environmental related accidents. The site-specific AMP includes a description of emergency response procedures, management of accidental emissions (such as spills) and registration and assessment of accidents.
|  |  | a) protection measures |  | Yes |  | See above
|  |  | b) Management of incidental/accidental emissions |  | Yes |  | See above
|  |  | c) Incident/accident registration and assessment system |  | Yes |  | See above
22 | Material efficiency | Material efficiency Applicability Some applicability limitations derive from the risk of contamination posed by the presence of impurities (e.g. heavy metals, POPs, salts, pathogens) in the waste that substitutes other materials. Another limitation is the compatibility of the waste substituting other materials with the waste input (see BAT 2). | In order to use materials efficiently, BAT is to substitute materials with waste. |  | Yes |  | Treated final effluent produced by the wastewater treatment works will be used on the site wherever possible instead of potable water. Waste heat is used in steam boilers and pre THP dilution.
23 | Energy efficiency | Energy efficiency techniques | In order to use energy efficiently, BAT is to use both of the techniques given below.
|  |  | a) energy efficient plan |  | Yes |  | Monthly reports (e.g. engine efficiences) specifically on energy to ensure plant is efficient. Energy efficiency regularly reviewed in line with permit requirements. KPIs with set performance targets in place.
|  |  | b) energy balance record |  | Yes |  | NWL have a energy balance record that provides a breakdown of the energy consumption and generation by the type of source This includes: (i) information on energy consumption in terms of delivered energy; (ii) information on energy exported from the installation; (iii) energy flow information showing how the energy is used throughout the process.
24 | Reuse of packaging | Reuse of packaging Applicability Some applicability restrictions derive from the risk of contamination of the waste posed by the reused packaging. | In order to reduce the quantity of waste sent for disposal, BAT is to maximise the reuse of packaging, as part of the residues management plan (see BAT 1). |  | N/A (explain) |  | Main feedstock is sludge - a waste that is not packaged. Other consumables' packaging is small but recycling is implemented where possible to comply with NWL Zero Avoidable Waste Strategy. Most chemicals will be designed to be delivered in bulk, thus minimising the requirement for oil/chemical drums, containers, IBC's etc. However, where these are used, they would always be returned to the supplier where possible for cleaning and reuse.
General BAT conclusions for the biological treatment of waste
33 | Overall performance |  | In order to reduce odour emissions and to improve the overall environmental performance, BAT is to select the waste input. |  | Yes |  | Howdon primary and secondary sludge is combined with imported tankered sludge in sludge holding tanks which are mixed using compressed air. This sludge is monitored for suitability for the treatment process and the treatment process is itself closely monitored. Any issues (e.g. foaming, unusual odours etc.) would be quickly observed by experienced operators.
34 | Emissions to air |  | In order to reduce channelled emissions to air of dust, organic compounds and odorous compounds, including H2S and NH3, BAT is to use one or a combination of the techniques given below. | See 'Air emissions tables' tab
|  |  | a) adsorption - see table 6.1 |  | Yes |  | Activated carbon used for treatment of off gas from biogas upgrade plant.
|  |  | b) biofilter - see table 6.1 |  | Yes |  | All odouriferous areas are force ventilated and extracted "air" treated by biofilter.
|  |  | c) fabric filter - see table 6.1 |  | N/A (explain) |  | Other techniques used, see above.
|  |  | d) thermal oxidation - see table 6.1 |  | N/A (explain) |  | Other techniques used, see above.
|  |  | e) wet scrubbing - see table 6.1 |  | N/A (explain) |  | Other techniques used, see above.
35 | Emissions to water and usage |  | In order to reduce the generation of waste water and to reduce water usage, BAT is to use all of the techniques given below.
|  |  | a) segregation of water streams |  | N/A (explain) |  | All waste waters on site return to head of works via sumps to remove chance of pollution to river in case of spillage.
|  |  | b) water recirculation |  | Yes |  | Reuse of final effluent where appropriate. Returns to head of the works.
|  |  | c) minimisation of the generation of leachate |  | N/A (explain) |  | No leachate
BAT conclusions for the anaerobic treatment of waste
38 | Emissions to air | Monitor and control key waste and process parameters | In order to reduce emissions to air and to improve the overall environmental performance, BAT is to monitor and/or control the key waste and process parameters. |  | Yes |  | Already monitor/control emissions to air and report to EA. Monitored by use of SCADA - level pressures and flows. Monitoring of pH, alkalinity, VFAs. Biogas quantity and composition (H2S) Temperature, liquid levels, foam levels in the digester.
Description of techniques for diffuse emissions of organic compounds to air
| Leak detection and repair (LDAR) programme | For the control of volatile organic compounds | A structured approach to reduce fugitive emissions of organic compounds by detection and subsequent repair or replacement of leaking components. Currently, sniffing (described by EN 15446) and optical gas imaging methods are available for the identification of leaks. Sniffing method: The first step is the detection using hand-held organic compound analysers measuring the concentration adjacent to the equipment (e.g. using flame ionisation or photoionisation). The second step consistsof enclosing the component in an impermeable bag to carry out a direct measurement at the source of the emission. This second step is sometimes replaced by mathematical correlation curves derived from statistical results obtained from a large number of previous measurements made on similar components. Optical gas imaging methods: Optical imaging uses small lightweight hand-held cameras which enable the visualisation of gas leaks in real time, so that they appear as ‘smoke’ on a video recorder together with the normal imageof the component concerned, to easily and rapidly locate significant organic compound leaks. Active systems produce an image with a backscattered infrared laser light reflected on the component and its surroundings. Passive systems are based on the natural infrared radiation of the equipment and its surroundings. |  | To be implemented |  | Operations utilise a combination of SCADA monitoring/alarms/daily walkarounds/occasional leak detection (leak detection & CCTV). A LDAR Plan is in development in accordance with the Environment Agency Appropriate Measuers for Biological Waste and will be available for issue by 30th June 2023.
Description of techniques for management techniques
| Accident management plan |  | The accident management plan is part of the EMS (see BAT 1) and identifies hazards posed by the plant and the associated risks and defines measures to address these risks. It considers the inventory of pollutants present or likely to be present which could have environmental consequences if they escape |  | Yes |  | Company and Site Specific Emergency plan with additional local resources available (as well as normal emergency services). The Site operates under a site-specific Accident Management Plan, referred to by Northumbrian Water as the Site Emergency Incident Plan, to prevent and manage environmental related accidents. The site-specific AMP includes a description of emergency response procedures, management of accidental emissions (such as spills) and registration and assessment of accidents.
| Residues management plan |  | A residues management plan is part of the EMS (see BAT 1) and is a set of measures aiming to (1) minimise the generation of residues arising from the treatment of waste; (2) optimise the reuse, regeneration, recycling and/or recovery of energy of the residues, and (3) ensure the proper disposal of residues. |  | To be implemented |  | Residues MP as part of EMS. Resultant Digestate is a useful product for agricultural and land conditioning use. Odours captured and returned to process for treatment.

## AMP
Accident prevention and management plan
You need a plan for dealing with any incidents or events that could result in:
pollution
not being able to comply with your permit
The plan must identify potential accidents, for example:
equipment breakdowns
enforced shutdowns
fires
vandalism
flooding
any other incident which causes an unexpected change to normal operations, such as extreme weather
For each potential incident, it must also state the:
likelihood of the accident happening
consequences of the accident happening
measures you’ll take to avoid the accident happening
measures you’ll take to minimise the impact if the accident does happen
Your accident plan must also say how you will record, investigate and respond to accidents or breaches of your permit.
Your accident plan must also include:
the date it was reviewed
when it will next be reviewed
a list of emergency contacts and how to reach them
a list of substances stored at your site, and your storage facilities
forms to record accidents on
Consider taking the following actions, if you think they are relevant to the operations you carry out at your site:
make emergency services aware of your activities
take out insurance to cover the cost of clean up following an accident
check whether you’re in a flood risk area and sign up for flood warnings
develop a system to allow access to important information away from your site
Online security: protect your business
You can take some simple steps to protect your business against online security threats. Good online security will help make sure your business does not cause pollution. Any pollution that does occur is your responsibility as the permit holder.
See the National Cyber Security Centre website for guidance about online security.
Contact information for the public
If you have a waste or installations permit you must display a notice board at or near the site entrance telling the public about the site. It must include:
the permit holder’s name (company name at least)
an emergency contact name and telephone number
a statement that the site is permitted by the Environment Agency
the permit number
Environment Agency telephone number 03708 506506 and the incident hotline 0800 807060 (or another number we subsequently tell you about in writing)
A notice board is optional for other permits and will depend on whether you consider that the public will need to see emergency contact information at your site.

## Water emission tables
This information only shows monitoring and AELs associated with certain treatments
BAT 7
Monitoring emissions to water
| Substance/parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency (11)(12) | Monitoring associated with
| Chemical oxygen demand (COD) (15) (16) | No EN standard available | All waste treatments except treatment of water-based liquid waste | Once every month | BAT 20
| Arsenic (As), Cadmium (Cd), Chromium (Cr), Copper (Cu), Nickel (Ni), Lead (Pb), Zinc (Zn) (13) (14) | Various EN standards available (e.g. EN ISO 11885, EN ISO 17294-2, EN ISO 15586) | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste | Once every month
| Mercury (Hg) (13) (14) | Various EN standards available (i.e. EN ISO 17852, EN ISO 12846) | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste | Once every month
| PFOA (13) | No EN standard available | All waste treatments | Once every six months
PFOS (13)
| Total nitrogen (Total N) (16) | EN 12260, EN ISO 11905-1 | Biological treatment of waste | Once every month
| Total organic carbon (TOC) (15) (16) | EN 1484 | All waste treatments except treatment of water-based liquid waste | Once every month
| Total phosphorus (Total P) (16) | Various EN standards available (i.e. EN ISO 15681-1 and -2, EN ISO 6878, EN ISO 11885) | Biological treatment of waste | Once every month
| Total suspended solids (TSS) (16) | EN 872 | All waste treatments except treatment of water-based liquid waste | Once every month
(11) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(12) In the case of batch discharge less frequent than the minimum monitoring frequency, monitoring is carried out once per batch.
(13) The monitoring only applies when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(14) In the case of an indirect discharge to a receiving water body, the monitoring frequency may be reduced if the downstream waste water treatment plant abates the pollutants concerned.
(15) Either TOC or COD is monitored. TOC is the preferred option, because its monitoring does not rely on the use of very toxic compounds.
(16) The monitoring applies only in the case of a direct discharge to a receiving water body.
BAT 20
Table 6.1 BAT-associated emission levels (BAT-AELs) for direct discharges to a receiving water body
| Substance/Parameter | BAT-AEL (24) | Waste treatment process to which the BAT-AEL applies
| Total organic carbon (TOC) (25) | 10-60 mg/l | All waste treatments except treatment of water-based liquid waste
| Chemical oxygen demand (COD) (25) | 30-180 mg/l | All waste treatments except treatment of water-based liquid waste
| Total suspended solids (TSS) | 5-60 mg/l | All waste treatments
| Total nitrogen (Total N) | 1-25 mg/l (28) (29) | Biological treatment of waste
| Total phosphorus (Total P) | 0.3-2 mg/l | Biological treatment of waste
|  | 1-3 mg/l (27) | Treatment of water-based liquid waste
| Metals and metalliods (31) |  | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste
| Arsenic (expressed as As) | 0.01 - 0.05 mg/l
| Cadmium (expressed as Cd) | 0.01 - 0.05 mg/l
| Chromium (expressed as Cr) | 0.01 - 0.15 mg/l
| Copper (expressed as Cu) | 0.05 - 0.5 mg/l
| Lead (expressed as Pb) | 0.05 - 0.1 mg/l (32)
| Nickel (expressed as Ni) | 0.05 - 0.5 mg/l
| Mercury (expressed as Hg) | 0.5 - 5 ug/l
| Zinc (expressed as Zn) | 0.1 - 1 mg/l (33)
(24) The averaging periods are defined in the General considerations.
(25) Either the BAT-AEL for COD or the BAT-AEL for TOC applies. TOC monitoring is the preferred option because it does not rely on the use of very toxic compounds.
(27) The BAT-AEL may not apply to plants treating drilling muds/cuttings.
(28) The BAT-AEL may not apply when the temperature of the waste water is low (e.g. below 12 °C).
(29) The BAT-AEL may not apply in the case of high chloride concentrations (e.g. above 10 g/l in the waste input).
(31) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(32) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(33) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.
Table 6.2 BAT-associated emission levels (BAT-AELs) for indirect discharges to a receiving water body
| Substance/Parameter | BAT-AEL (24) | Waste treatment process to which the BAT-AEL applies
| Metals and metalliods (36) |  | Mechanical bilogical treatment of waste, Physico-chemical treatment of solid and/or pasty waste
| Arsenic (expressed as As) | 0.01 - 0.05 mg/l
| Cadmium (expressed as Cd) | 0.01 - 0.05 mg/l
| Chromium (expressed as Cr) | 0.01 - 0.15 mg/l
| Copper (expressed as Cu) | 0.05 - 0.5 mg/l
| Lead (expressed as Pb) | 0.05 - 0.1 mg/l (37)
| Nickel (expressed as Ni) | 0.05 - 0.5 mg/l
| Mercury (expressed as Hg) | 0.5 - 5 ug/l
| Zinc (expressed as Zn) | 0.1 - 1 mg/l (38)
(36) The BAT-AELs only apply when the substance concerned is identified as relevant in the waste water inventory mentioned in BAT 3.
(37) The upper end of the range is 0,3 mg/l for mechanical treatment in shredders of metal waste.
(38) The upper end of the range is 2 mg/l for mechanical treatment in shredders of metal waste.

## Air emission tables
This information only shows monitoring and AELs associated with certain treatments
BAT 8
Monitoring channelled emissions to air
| Substance/ Parameter | Standard(s) | Waste treatment process | Minimum monitoring frequency (17) | Monitoring associated with
| Dust | EN 13284-1 | Mechanical biological treatment of waste | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste | Once every six months | BAT 41
| H2S | No EN standard available | Biological treatment of waste (20) | Once every six months | BAT 34
| NH3 | No EN standard available | Biological treatment of waste (20) | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste (18) | Once every six months | BAT 41
| Odour concentration | EN 13725 | Biological treatment of waste (21) | Once every six months | BAT 34
| TVOC | EN 12619 | Mechanical biological treatment of waste | Once every six months | BAT 34
|  |  | Physico-chemical treatment of solid and/or pasty waste (18) | Once every six months | BAT 41
(17) Monitoring frequencies may be reduced if the emission levels are proven to be sufficiently stable.
(18) The monitoring only applies when the substance concerned is identified as relevant in the waste gas stream based on the inventory mentioned in BAT 3.
(20) The odour concentration may be monitored instead.
(21) The monitoring of NH3 and H2S can be used as an alternative to the monitoring of the odour concentration.
BAT 34
Table 6.7 BAT-associated emission levels (BAT-AELs) for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste
| Parameter | Unit | BAT-AEL (average over sampling period) | Waste treatment process
| NH3 (41) (42) | mg/Nm3 | 0.3 - 20 | All biological treatments of waste
| Odour concentration (41) (2) | ouE/Nm3 | 200 - 1,000
| Dust | mg/Nm3 | 2 - 5 | Mechanical biological treatments of waste
| TVOC | mg/Nm3 | 5 - 40 (43)
(41) Either the BAT-AEL for NH3 or the BAT-AEL for the odour concentration applies.
(42) This BAT-AEL does not apply to the treatment of waste mainly composed of manure.
(43) The lower end of the range can be achieved by using thermal oxidation.
BAT 41
BAT-associated emission level (BAT-AEL) for channelled emissions of dust to air from the physico-chemical treatment of solid and/or pasty waste
| Parameter | Unit | BAT-AEL (Average over the sampling period)
| Dust | mg/Nm3 | 2 - 5
Associated monitoring given in BAT 8

## Picklists
Narrative BATCs | Numeric BATCs | Derogation
Yes | Yes | Yes
To be implemented | To be implemented | No
Other (explain) | Other (explain) | NA
N/A (explain) | N/A (explain)
ADD A NOT APPLIC OPTION | for some