## Direct
H1 Assessment | Direct discharge to the River Aire from the RO plant
Guidance doc: | https://www.gov.uk/guidance/surface-water-pollution-risk-assessment-for-your-environmental-permit
STEP 1 - is RC > 10% EQS
RC- Effluent concentration ug/l (discharge form the RO)
Discharge Consent Parameters | Units | Average Concentration µg/l | RC | EQS - AA | 10%EQS | RC>10%EQS | Compliance Target Source
Ammoniacal Nitrogen [EQS based on correction for ammonia] | µg/l | 1270 | 1270 | 620 | 62 | FAIL | WFD (Standards and Classification) 2015
Chloride | µg/l | 2600 | 2600 | 250000 | 25000 | PASS | WFD (Standards and Classification) 2015
Sulphate | µg/l | 5300 | 5300 | 400000 | 40000 | PASS | WFD (Standards and Classification) 2015
Arsenic | µg/l | 4 | 4 | 50 | 5 | PASS | WFD (Standards and Classification) 2015
Cadmium | µg/l | 0.08 | 0.08 | 0.09 | 0.009 | FAIL | WFD (Standards and Classification) 2015
Chromium | µg/l | 2.5 | 2.5 | 4.7 | 0.47 | FAIL | WFD (Standards and Classification) 2015
Copper | µg/l | 7 | 7 | 1 | 0.1 | FAIL | WFD (Standards and Classification) 2015
Iron | µg/l | 17 | 17 | 1000 | 100 | PASS | WFD (Standards and Classification) 2015
Zinc | µg/l | 22.4 | 22.4 | 13.8 | 1.38 | FAIL | WFD (Standards and Classification) 2015
Phosphate | µg/l | 34.6 | 34.6 | 113 | 11.3 | FAIL | WFD (Standards and Classification) 2015
WFD (Standards and Classification) 2015
WFD (Standards and Classification) 2015
WFD (Standards and Classification) 2015
Sewerage Treatment Reduction Factor
Parameter | Average Concentration µg/l | Percentage removal rate of substance by activated sludge plant (STRF) | Proportion remaining in activated sludge plant | RC value (µg/l)
Ammoniacal Nitrogen | 1270 | N/A | N/A | #VALUE!
Chloride | 2600 | N/A | N/A | #VALUE!
Sulphate | 5300 | N/A | N/A | #VALUE!
Arsenic | 4 | N/A | N/A | #VALUE!
Cadmium | 0.08 | N/A | N/A | #VALUE!
Chromium | 2.5 | N/A | N/A | #VALUE!
Copper | 7 | N/A | N/A | #VALUE!
Iron | 17 | N/A | N/A | #VALUE!
Zinc | 22.4 | N/A | N/A | #VALUE!
Phosphate | 34.6 | N/A | N/A | #VALUE!
0
0
STEP 2 - is PC<4% EQS
where PC = EFR*RC/(EFR+RFR)
EFR - effluent flow rate (m3/sec) - average over 24 opertaion | 0.011574 | 1000 | m3/day
intermittent discharge - hours per day | N/A
number of days per week discharge | 7
EFR - effluent flow rate (m3/sec) - average - for intermittent discharge | N/A
RFR - river flow rate (Q95) (m3/sec) | 9.656
RFR - river flow rate (Q70) (m3/sec) | 16.8
Parameter | Units | RC | PC | EQS | 4%EQS | PC > 4%EQS
Ammoniacal Nitrogen | µg/l | 1270 | 1.5205 | 620 | 24.8 | PASS
Chloride | µg/l | 2600 | 3.1127 | 250000 | 10000 | PASS
Sulphate | µg/l | 5300 | 6.3452 | 400000 | 16000 | PASS
Arsenic | µg/l | 4 | 0.0047888 | 50 | 2 | PASS
Cadmium | µg/l | 0.08 | 9.5776e-05 | 0.09 | 0.0036 | PASS
Chromium | µg/l | 2.5 | 0.002993 | 4.7 | 0.188 | PASS
Copper | µg/l | 7 | 0.0083804 | 1 | 0.04 | PASS
Iron | µg/l | 17 | 0.020352 | 1000 | 40 | PASS
Zinc | µg/l | 22.4 | 0.026817 | 13.8 | 0.552 | PASS
Phosphate | µg/l | 34.6 | 0.041423 | 113 | 4.52 | PASS
STEP 3 - is (PEC -BC) > 10%EQS
where PEC*=((EFR*RC)+(RFR*BC))/(EFR+RFR) - this is only necessary where RFR<10*EFR
PEC = PC +BC
BC - background concentration - half EQS concentration
Parameter | Units | PC | BC | PEC | PEC* | PEC-BC | EQS | 10%EQS | PEC-BC > 10%EQS
Ammoniacal Nitrogen | µg/l | 1.5205 | 310 | 311.5205 | 309.6307 | 1.5205 | 620 | 62 | PASS
Chloride | µg/l | 3.1127 | 125000 | 125003.1127 | 124850.353 | 3.1127 | 250000 | 25000 | PASS
Sulphate | µg/l | 6.3452 | 200000 | 200006.3452 | 199760.5665 | 6.3452 | 400000 | 40000 | PASS
Arsenic | µg/l | 0.0047888 | 25 | 25.0048 | 24.9701 | 0.0047888 | 50 | 5 | PASS
Cadmium | µg/l | 9.5776e-05 | 0.045 | 0.045096 | 0.044946 | 9.5776e-05 | 0.09 | 0.009 | PASS
Chromium | µg/l | 0.002993 | 2.35 | 2.353 | 2.3472 | 0.002993 | 4.7 | 0.47 | PASS
Copper | µg/l | 0.0083804 | 0.5 | 0.50838 | 0.49941 | 0.0083804 | 1 | 0.1 | PASS
Iron | µg/l | 0.020352 | 500 | 500.0204 | 499.4014 | 0.020352 | 1000 | 100 | PASS
Zinc | µg/l | 0.026817 | 6.9 | 6.9268 | 6.8918 | 0.026817 | 13.8 | 1.38 | PASS
Phosphate | µg/l | 0.041423 | 56.5 | 56.5414 | 56.4324 | 0.041423 | 113 | 11.3 | PASS
STEP 4 - is PEC > EQS
Parameter | Units | PC | BC | PEC |  |  | EQS |  | PEC>EQS
Ammoniacal Nitrogen | µg/l | 1.5205 | 310 | 311.5205 |  |  | 620 |  | PASS
Chloride | µg/l | 3.1127 | 125000 | 125003.1127 |  |  | 250000 |  | PASS
Sulphate | µg/l | 6.3452 | 200000 | 200006.3452 |  |  | 400000 |  | PASS
Arsenic | µg/l | 0.0047888 | 25 | 25.0048 |  |  | 50 |  | PASS
Cadmium | µg/l | 9.5776e-05 | 0.045 | 0.045096 |  |  | 0.09 |  | PASS
Chromium | µg/l | 0.002993 | 2.35 | 2.353 |  |  | 4.7 |  | PASS
Copper | µg/l | 0.0083804 | 0.5 | 0.50838 |  |  | 1 |  | PASS
Iron | µg/l | 0.020352 | 500 | 500.0204 |  |  | 1000 |  | PASS
Zinc | µg/l | 0.026817 | 6.9 | 6.9268 |  |  | 13.8 |  | PASS
Phosphate | µg/l | 0.041423 | 56.5 | 56.5414 |  |  | 113 |  | PASS
Screening test: ‘priority hazardous pollutants’
Average flow - litres per day | 1000000
Pollutant | Annual significant load limit in kg | Average concentration (mg/l) | Loading per year (kg)
Cadmium | 5 | 8e-05 | 2.92e-05

## Sewer
H1 Assessment | Discharge to the sewer from the Biological Treatment Plant
Guidance doc: | https://www.gov.uk/guidance/surface-water-pollution-risk-assessment-for-your-environmental-permit
STEP 1 - is RC > 10% EQS
RC- Effluent concentration ug/l
Discharge Consent Parameters | Units | Average concentration µg/l | RC | EQS - AA | 10%EQS | RC>10%EQS | Compliance Target Source
Ammoniacal Nitrogen [based on correction for ammonia] | µg/l | 440 | 35.2 | 620 | 62 | PASS | WFD (Standards and Classification) 2015
Chloride | µg/l | 2164 | 2164 | 250000 | 25000 | PASS | WFD (Standards and Classification) 2015
Sulphate | µg/l | 323250 | 323250 | 400000 | 40000 | FAIL | WFD (Standards and Classification) 2015
Arsenic | µg/l | 57 | 50.73 | 50 | 5 | FAIL | WFD (Standards and Classification) 2015
Cadmium | µg/l | 0.45 | 0.4005 | 0.09 | 0.009 | FAIL | WFD (Standards and Classification) 2015
Chromium | µg/l | 106 | 16.96 | 4.7 | 0.47 | FAIL | WFD (Standards and Classification) 2015
Copper | µg/l | 14.2 | 2.982 | 1 | 0.1 | FAIL | WFD (Standards and Classification) 2015
Iron | µg/l | 997 | 767.69 | 1000 | 100 | FAIL | WFD (Standards and Classification) 2015
Lead | µg/l | 7.6 | 1.292 | 1.2 | 0.12 | FAIL | WFD (Standards and Classification) 2015
Nickel | µg/l | 152 | 115.52 | 4 | 0.4 | FAIL | WFD (Standards and Classification) 2015
Zinc | µg/l | 22.4 | 7.392 | 13.8 | 1.38 | FAIL | WFD (Standards and Classification) 2015
Phosphorous | µg/l | 7750 | 6200 | 148 | 14.8 | FAIL | WFD (Standards and Classification) 2015
Mecoprop | µg/l | 50.3 | 50.3 | 18 | 1.8 | FAIL | WFD (Standards and Classification) 2015
Sewerage Treatment Reduction Factor
Parameter | Average concentration (µg/l) | Percentage removal rate of substance by activated sludge plant (STRF) | Proportion remaining in activated sludge plant | RC value (µg/l)
Ammoniacal Nitrogen | 440 | 92 | 0.08 | 35.2
Chloride | 2164 | 0 | 1 | 2164
Sulphate (no STRF - assumed 0) | 323250 | 0 | 1 | 323250
Arsenic | 57 | 11 | 0.89 | 50.73
Cadmium | 0.45 | 11 | 0.89 | 0.4005
Chromium | 106 | 84 | 0.16 | 16.96
Copper | 14.2 | 79 | 0.21 | 2.982
Iron | 997 | 23 | 0.77 | 767.69
Lead | 7.6 | 83 | 0.17 | 1.292
Nickel | 152 | 24 | 0.76 | 115.52
Zinc | 22.4 | 67 | 0.33 | 7.392
Phosphorous | 7750 | 20 | 0.8 | 6200
Mecoprop | 50.3 | 0 | 1 | 50.3
STEP 2 - is PC<4% EQS
where PC = EFR*RC/(EFR+RFR)
EFR - effluent flow rate (m3/sec) | 0.011574 | 1000 | m3/day
intermittent discharge - hours per day | N/A
number of days per week discharge | 7
EFR - effluent flow rate (m3/sec) - average - for intermittent discharge | N/A
RFR - river flow rate (Q95) (m3/sec) | 9.656
RFR - river flow rate (Q70) (m3/sec) | 16.8
Parameter | Units | RC | PC | EQS | 4%EQS | PC > 4%EQS
Ammoniacal Nitrogen | µg/l | 35.2 | 0.042142 | 620 | 24.8 | PASS
Chloride | µg/l | 2164 | 2.5908 | 250000 | 10000 | PASS
Sulphate | µg/l | 323250 | 386.9967 | 400000 | 16000 | PASS
Arsenic | µg/l | 50.73 | 0.060734 | 50 | 2 | PASS
Cadmium | µg/l | 0.4005 | 0.00047948 | 0.09 | 0.0036 | PASS
Chromium | µg/l | 16.96 | 0.020305 | 4.7 | 0.188 | PASS
Copper | µg/l | 2.982 | 0.0035701 | 1 | 0.04 | PASS
Iron | µg/l | 767.69 | 0.91908 | 1000 | 40 | PASS
Lead | µg/l | 1.292 | 0.0015468 | 1.2 | 0.048 | PASS
Nickel | µg/l | 115.52 | 0.1383 | 4 | 0.16 | PASS
Zinc | µg/l | 7.392 | 0.0088497 | 13.8 | 0.552 | PASS
Phosphorous | µg/l | 6200 | 7.4227 | 148 | 5.92 | FAIL
Mecoprop | µg/l | 50.3 | 0.060219 | 18 | 0.72 | PASS
STEP 3 - is (PEC -BC) > 10%EQS
where PEC*=((EFR*RC)+(RFR*BC))/(EFR+RFR) - this is only necessary where RFR<10*EFR
PEC = PC +BC
BC - background concentration - half EQS concentration
Parameter | Units | PC | BC | PEC | PEC* | PEC-BC | EQS | 10%EQS | PEC-BC > 10%EQS
Ammoniacal Nitrogen | µg/l | 0.042142 | 310 | 310.0421 | 309.6289 | 0.042142 | 620 | 62 | PASS
Chloride | µg/l | 2.5908 | 125000 | 125002.5908 | 124850.3524 | 2.5908 | 250000 | 25000 | PASS
Sulphate | µg/l | 386.9967 | 200000 | 200386.9967 | 199761.0222 | 386.9967 | 400000 | 40000 | PASS
Arsenic | µg/l | 0.060734 | 25 | 25.0607 | 24.9701 | 0.060734 | 50 | 5 | PASS
Cadmium | µg/l | 0.00047948 | 0.045 | 0.045479 | 0.044947 | 0.00047948 | 0.09 | 0.009 | PASS
Chromium | µg/l | 0.020305 | 2.35 | 2.3703 | 2.3472 | 0.020305 | 4.7 | 0.47 | PASS
Copper | µg/l | 0.0035701 | 0.5 | 0.50357 | 0.49941 | 0.0035701 | 1 | 0.1 | PASS
Iron | µg/l | 0.91908 | 500 | 500.9191 | 499.4025 | 0.91908 | 1000 | 100 | PASS
Lead | µg/l | 0.0015468 | 0.6 | 0.60155 | 0.59928 | 0.0015468 | 1.2 | 0.12 | PASS
Nickel | µg/l | 0.1383 | 2 | 2.1383 | 1.9978 | 0.1383 | 4 | 0.4 | PASS
Zinc | µg/l | 0.0088497 | 6.9 | 6.9088 | 6.8917 | 0.0088497 | 13.8 | 1.38 | PASS
Phosphorous | µg/l | 7.4227 | 74 | 81.4227 | 73.9203 | 7.4227 | 148 | 14.8 | PASS
Mecoprop | µg/l | 0.060219 | 9 | 9.0602 | 8.9893 | 0.060219 | 18 | 1.8 | PASS
STEP 4 - is PEC > EQS
Parameter | Units | PC | BC | PEC |  |  | EQS |  | PEC>EQS
Ammoniacal Nitrogen | µg/l | 0.042142 | 310 | 310.0421 |  |  | 620 |  | PASS
Chloride | µg/l | 2.5908 | 125000 | 125002.5908 |  |  | 250000 |  | PASS
Sulphate | µg/l | 386.9967 | 200000 | 200386.9967 |  |  | 400000 |  | PASS
Arsenic | µg/l | 0.060734 | 25 | 25.0607 |  |  | 50 |  | PASS
Cadmium | µg/l | 0.00047948 | 0.045 | 0.045479 |  |  | 0.09 |  | PASS
Chromium | µg/l | 0.020305 | 2.35 | 2.3703 |  |  | 4.7 |  | PASS
Copper | µg/l | 0.0035701 | 0.5 | 0.50357 |  |  | 1 |  | PASS
Iron | µg/l | 0.91908 | 500 | 500.9191 |  |  | 1000 |  | PASS
Lead | µg/l | 0.0015468 | 0.6 | 0.60155 |  |  | 1.2 |  | PASS
Nickel | µg/l | 0.1383 | 2 | 2.1383 |  |  | 4 |  | PASS
Zinc | µg/l | 0.0088497 | 6.9 | 6.9088 |  |  | 13.8 |  | PASS
Phosphorous | µg/l | 7.4227 | 74 | 81.4227 |  |  | 148 |  | PASS
Mecoprop | µg/l | 0.060219 | 9 | 9.0602 |  |  | 18 |  | PASS
Screening test: ‘priority hazardous pollutants’
Average flow - litres per day | 1000000
Pollutant | Annual significant load limit in kg | Average concentration (mg/l) | Loading per year (kg)
Cadmium | 5 | 0.00045 | 0.00016425