Application information requirements for assessing air emissions from biomass boilers at EPR intensive farms

Required information

Please supply the following information:

| Number of biomass boilers | 1 |
| --- | --- |
| Stack height (from ground level) | 10m |
| Thermal input in MW or kW of each boiler | 1093kW |
| The exact grid reference(s) of the stack(s) | SO 58851 63430 |
| The exact grid reference of the centre of the farm | SO 58713 63460 |
| A plan giving layout of the farm including dimensions. | Attached |
| Fuel type (virgin wood, straw or miscanthus) | Straw |
| Approximate fuel storage tonnage | 10 tonnes |
| Details of accident prevention measures - please provide risk assessment document |  |
| Confirmation that the ash will be disposed of as a waste, or spread under an exemption | Spread under exemption |
| Confirmation that the boiler and its installation meet the technical criteria to be eligible for the Renewable Heat Incentive (the boiler manufacturer should have proof of certification) please provide certificate | Attached |
| Additional information required only if the boilers do not screen out as detailed in the guidance at https://www.gov.uk/guidance/intensive-farming-risk-assessment-for-your-environmental-permit#air-emissions-biomass-boilers |
| Adjacent Building heights | 9m |
| Flue diameter | ID 350mm tapered to 275mm |
| Flue gas exit minimum temperature | 170°c |
| Exit velocity in m/sec | 16 m/s |
| NOx concentration in mg/Nm3 | 224 |
| CO concentration in mg/Nm3 | 17 |
| PM10 (dust) concentration in mg/Nm3 | 15 |
| O2 concentration % | 10% |

(Please note the ‘N’ in Nm³ means ‘normal’ which means the gas volume, which depends on temperature and pressure, is measured at 101.325 kPa and 0 °C)