## On-Site Source Spot Meas's
SOURCE SPOT MEASUREMENT RESULTS - LINEAR 1/3 OCTAVES | [60 empty] | Summary of Results
| Meas. Ref. | 1 |  |  |  |  | Meas. Ref. | 2 |  |  |  |  | Meas. Ref. | 3 |  |  |  |  | Meas. Ref. | 4 |  |  |  |  | Meas. Ref. | 5 |  |  |  |  | Meas. Ref. | 6 |  |  |  |  | Meas. Ref. | 7 |  |  |  |  | Meas. Ref. | 8 |  |  |  |  | Meas. Ref. | 9 |  |  |  |  | Meas. Ref. | 10
| Source | Compressor |  |  |  |  | Source | Generator |  |  |  |  | Source | Flare Stack and Generator |  |  |  |  | Source | Flare Stack and Generator |  |  |  |  | Source | Flare Stack and Generator + Compressor |  |  |  |  | Source | Flare Stack |  |  |  |  | Source | Flare Stack |  |  |  |  | Source | Flare Stack |  |  |  |  | Source | Flare Stack |  |  |  |  | Source | Flare Stack with Compressor
| Location | Right |  |  |  |  | Location | - |  |  |  |  | Location | Front |  |  |  |  | Location | Back |  |  |  |  | Location | Back |  |  |  |  | Location | Front |  |  |  |  | Location | Front |  |  |  |  | Location | Left |  |  |  |  | Location | Right |  |  |  |  | Location | Right | [9 empty] | Octave Band Spectra - LINEAR
| Distance (m) | 2 |  |  |  |  | Distance (m) | 5 |  |  |  |  | Distance (m) | 10 |  |  |  |  | Distance (m) | 3 |  |  |  |  | Distance (m) | 3 |  |  |  |  | Distance (m) | 2 |  |  |  |  | Distance (m) | 5 |  |  |  |  | Distance (m) | 5 |  |  |  |  | Distance (m) | 2 |  |  |  |  | Distance (m) | 5 |  |  |  |  | Meas. Ref. | Plant | Direction | Condition | Distance (m) | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LAeq,T | LWA | Notes | All Flare stack measurements included contribution from the 'Elec Plant' (generator)
| Notes | - |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | Includes Compressor |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | NORMAL |  |  |  |  | Notes | - |  |  |  |  | 1 | Compressor | Right | - | 2 | 67.7 | 71 | 68.2 | 67.5 | 64 | 64.9 | 60.8 | 61.5 | 56.7 | 50.2 | 69.6 | 83.6206 | Use for Compressor | Compressor kicked in and out so in some measurements but not others (see file names)
[61 empty] | 2 | Generator | - | NORMAL | 5 | 77.5 | 71.8 | 78.6 | 72 | 68 | 59.7 | 56.5 | 51.6 | 43.9 | 41.5 | 68.9 | 90.8794 | Use for Generator | NORMAL' is 'without' the compressor
| File | Compressor Right Side 2m |  |  |  |  | File | Elecplant Front 5m Normal |  |  |  |  | File | Flare Stack and Elecplant Front 10m Norm... |  |  |  |  | File | Flare Stack Back 3m Normal |  |  |  |  | File | FLare Stack Back 3m With Compressor |  |  |  |  | File | Flare Stack Front 2m Normal |  |  |  |  | File | Flare Stack Front 5m Normal |  |  |  |  | File | Flare Stack Left Side 5m Normal |  |  |  |  | File | Flare STack Right Side 2m Normal |  |  |  |  | File | Flare Stack Right Side 5m With Compresso... |  |  |  |  | 3 | Flare Stack and Generator | Front | NORMAL | 10 | 80 | 68.1 | 65.6 | 59.5 | 52.6 | 49.3 | 47 | 43.5 | 37.7 | 40.1 | 56.7 | 84.7 |  | Direction is when looking from the access track
| Start | 2021-11-18 12:06 |  |  |  |  | Start | 2021-11-18 12:15 |  |  |  |  | Start | 2021-11-18 12:17 |  |  |  |  | Start | 2021-11-18 12:10 |  |  |  |  | Start | 2021-11-18 12:08 |  |  |  |  | Start | 2021-11-18 11:57 |  |  |  |  | Start | 2021-11-18 11:59 |  |  |  |  | Start | 2021-11-18 12:13 |  |  |  |  | Start | 2021-11-18 12:01 |  |  |  |  | Start | 2021-11-18 12:04 |  |  |  |  | 4 | Flare Stack and Generator | Back | NORMAL | 3 | 74.3 | 68.1 | 65.8 | 59.2 | 55.5 | 51.1 | 47.7 | 53.4 | 52.6 | 47.9 | 59.8 | 77.3424 |  | Right' is north east side (i.e. right side when looking on plan with north of plan pointing away from reader)
| End | 2021-11-18 12:07 |  |  |  |  | End | 2021-11-18 12:16 |  |  |  |  | End | 2021-11-18 12:18 |  |  |  |  | End | 2021-11-18 12:11 |  |  |  |  | End | 2021-11-18 12:08 |  |  |  |  | End | 2021-11-18 11:58 |  |  |  |  | End | 2021-11-18 11:59 |  |  |  |  | End | 2021-11-18 12:14 |  |  |  |  | End | 2021-11-18 12:03 |  |  |  |  | End | 2021-11-18 12:05 |  |  |  |  | 5 | Flare Stack and Generator and Compressor | Back | Includes Compressor | 3 | 79.2 | 74 | 66.4 | 61 | 58 | 57.2 | 54 | 56.6 | 55.6 | 50.1 | 63.5 | 81.0424 |  | Left' is South-west side (i.e. right side when looking on plan with north of plan pointing away from reader)
| Channel | Type | Wght | Unit | Leq | Octaves | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | Channel | Type | Wght | Unit | Leq |  | 6 | Flare Stack | Front | NORMAL | 2 | 83.2 | 76.2 | 67.7 | 72.6 | 64.6 | 61.5 | 51.3 | 49.5 | 41.4 | 40.8 | 68.1 | 82.1206
| Solo 061331 | Leq | A | dB | 69.6 |  | Solo 061331 | Leq | A | dB | 68.9 |  | Solo 061331 | Leq | A | dB | 56.7 |  | Solo 061331 | Leq | A | dB | 59.8 |  | Solo 061331 | Leq | A | dB | 63.5 |  | Solo 061331 | Leq | A | dB | 68.1 |  | Solo 061331 | Leq | A | dB | 60.6 |  | Solo 061331 | Leq | A | dB | 62 |  | Solo 061331 | Leq | A | dB | 61.2 |  | Solo 061331 | Leq | A | dB | 59.4 |  | 7 | Flare Stack | Front | NORMAL | 5 | 80.4 | 72.6 | 66.7 | 64.9 | 57.3 | 54.3 | 47.6 | 44.7 | 36.8 | 37.9 | 60.6 | 82.5794
| Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 67.6 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 76.1 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 78.8 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 72.3 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 77.6 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 81.4 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 79.3 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 81.8 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 76.5 |  | Solo 061331 | 1/3 Oct 20Hz | Lin | dB | 71.5 |  | 8 | Flare Stack | Left | NORMAL | 5 | 83.4 | 73.8 | 69.3 | 64.7 | 60.2 | 54.9 | 50.4 | 46.6 | 39.4 | 40.4 | 62 | 83.9794 | Use for Flare (Highest of indiviual flare measurements)
| Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 65.6 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 73.8 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 77.7 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 71.2 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 76.2 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 80 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 77.6 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 80.3 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 75.8 |  | Solo 061331 | 1/3 Oct 25Hz | Lin | dB | 70 |  | 9 | Flare Stack | Right | NORMAL | 2 | 79.3 | 73.4 | 66.6 | 64.2 | 59.3 | 55 | 45.7 | 41.2 | 35 | 35.4 | 61.2 | 75.2206
| Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 60.1 | 67.7 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 73.4 | 77.5 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 74.7 | 80 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 69.7 | 74.3 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 74.5 | 79.2 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 78.6 | 83.2 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 75.5 | 80.4 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 78.9 | 83.4 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 75 | 79.3 | Solo 061331 | 1/3 Oct 31.5Hz | Lin | dB | 68.9 | 73.1 | 10 | Flare Stack and Compressor | Right | - | 5 | 73.1 | 69.2 | 65.5 | 59.9 | 56.6 | 54 | 47.1 | 44.5 | 36.8 | 29.7 | 59.4 | 81.3794
| Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 61 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 70.1 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 70.4 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 66.7 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 71.4 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 75.5 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 72.3 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 75.2 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 71.8 |  | Solo 061331 | 1/3 Oct 40Hz | Lin | dB | 64.3
| Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 68 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 67.6 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 65.2 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 66.1 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 72.9 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 72.8 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 68.9 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 71.2 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 68.9 |  | Solo 061331 | 1/3 Oct 50Hz | Lin | dB | 65.5 | [6 empty] | Octave Band Sound Power Levels for Assessment
| Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 64 | 71 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 66.2 | 71.8 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 62.9 | 68.1 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 60.5 | 68.1 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 64.4 | 74 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 70.1 | 76.2 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 67.4 | 72.6 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 68.5 | 73.8 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 67.6 | 73.4 | Solo 061331 | 1/3 Oct 63Hz | Lin | dB | 63.4 | 69.2 | SOUND POWER LEVEL DATA
| Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 65.9 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 67.1 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 61 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 61.1 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 64.2 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 70.9 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 66.8 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 65.4 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 69.2 |  | Solo 061331 | 1/3 Oct 80Hz | Lin | dB | 64 |  | 1 | Compressor | Right | Distance | 2 | 81.7206 | 85.0206 | 82.2206 | 81.5206 | 78.0206 | 78.9206 | 74.8206 | 75.5206 | 70.7206 | 64.2206 | 83.6206
| Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 65.3 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 76.9 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 60.6 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 62.8 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 64 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 63.1 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 62.1 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 65.3 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 63.1 |  | Solo 061331 | 1/3 Oct 100Hz | Lin | dB | 62.2 |  | 2 | Generator | - | Distance | 5 | 99.4794 | 93.7794 | 100.5794 | 93.9794 | 89.9794 | 81.6794 | 78.4794 | 73.5794 | 65.8794 | 63.4794 | 90.8794
| Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 60.7 | 68.2 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 71.5 | 78.6 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 61.8 | 65.6 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 60.1 | 65.8 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 59.8 | 66.4 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 63 | 67.7 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 62 | 66.7 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 64.9 | 69.3 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 61.4 | 66.6 | Solo 061331 | 1/3 Oct 125Hz | Lin | dB | 60.8 | 65.5 | 8 | Flare Stack | Left | Distance | 5 | 105.3794 | 95.7794 | 91.2794 | 86.6794 | 82.1794 | 76.8794 | 72.3794 | 68.5794 | 61.3794 | 62.3794 | 83.9794
| Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 63 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 69.7 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 59.9 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 59.2 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 59.3 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 62.6 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 61.8 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 63.2 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 60.6 |  | Solo 061331 | 1/3 Oct 160Hz | Lin | dB | 58.4
| Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 60 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 67.5 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 57.6 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 57.2 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 57.8 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 65 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 63.4 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 62.4 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 59.5 |  | Solo 061331 | 1/3 Oct 200Hz | Lin | dB | 53.3
| Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 61.5 | 67.5 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 65.4 | 72 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 52 | 59.5 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 52.3 | 59.2 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 53.3 | 61 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 67 | 72.6 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 54.5 | 64.9 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 59 | 64.7 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 59.3 | 64.2 | Solo 061331 | 1/3 Oct 250Hz | Lin | dB | 53.6 | 59.9
| Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 65 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 68.3 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 52 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 51.6 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 56.6 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 70.1 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 57.9 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 56 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 59.4 |  | Solo 061331 | 1/3 Oct 315Hz | Lin | dB | 57.2
| Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 60.3 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 66.6 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 49.5 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 52.3 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 55.1 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 59.7 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 51.7 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 54.4 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 54.1 |  | Solo 061331 | 1/3 Oct 400Hz | Lin | dB | 49.8
| Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 59.4 | 64 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 60.8 | 68 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 47.8 | 52.6 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 51 | 55.5 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 52.7 | 58 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 58.5 | 64.6 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 52.8 | 57.3 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 57.3 | 60.2 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 54.9 | 59.3 | Solo 061331 | 1/3 Oct 500Hz | Lin | dB | 48.4 | 56.6
| Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 57.5 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 57.5 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 45 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 48 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 51 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 61 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 53 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 53.5 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 54.6 |  | Solo 061331 | 1/3 Oct 630Hz | Lin | dB | 54.6
| Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 57.7 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 55.8 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 46 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 46.7 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 51.8 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 59.6 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 52.5 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 52.3 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 53.2 |  | Solo 061331 | 1/3 Oct 800Hz | Lin | dB | 51
| Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 61.5 | 64.9 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 54.6 | 59.7 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 43.3 | 49.3 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 46.8 | 51.1 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 54.3 | 57.2 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 55.7 | 61.5 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 47.9 | 54.3 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 49.3 | 54.9 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 48.9 | 55 | Solo 061331 | 1/3 Oct 1kHz | Lin | dB | 48 | 54
| Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 60.4 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 54.3 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 43.8 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 45.4 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 50.1 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 50.9 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 45 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 47.4 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 44.6 |  | Solo 061331 | 1/3 Oct 1.25kHz | Lin | dB | 47.8
| Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 56.3 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 52.5 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 42.9 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 43.1 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 50.1 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 47.9 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 43.8 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 46.9 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 42.3 |  | Solo 061331 | 1/3 Oct 1.6kHz | Lin | dB | 43.4
| Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 55.3 | 60.8 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 52.3 | 56.5 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 42.3 | 47 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 42.7 | 47.7 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 49.7 | 54 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 46.6 | 51.3 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 43.2 | 47.6 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 45.9 | 50.4 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 41.3 | 45.7 | Solo 061331 | 1/3 Oct 2kHz | Lin | dB | 42.1 | 47.1
| Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 56.5 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 50 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 41.3 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 43 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 47.3 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 44.4 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 41.1 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 43.5 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 38.5 |  | Solo 061331 | 1/3 Oct 2.5kHz | Lin | dB | 41.2
| Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 54.2 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 49.2 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 40.5 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 49 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 51 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 43.1 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 40.9 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 43.4 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 37 |  | Solo 061331 | 1/3 Oct 3.15kHz | Lin | dB | 36.4
| Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 59.7 | 61.5 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 46.3 | 51.6 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 39 | 43.5 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 49.5 | 53.4 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 53.7 | 56.6 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 48 | 49.5 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 41.7 | 44.7 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 42.7 | 46.6 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 38.1 | 41.2 | Solo 061331 | 1/3 Oct 4kHz | Lin | dB | 43.2 | 44.5
| Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 53.2 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 42.6 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 35.1 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 46.8 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 49.9 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 38.2 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 33.9 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 37.2 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 32.4 |  | Solo 061331 | 1/3 Oct 5kHz | Lin | dB | 34.9
| Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 51.6 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 40.1 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 33.4 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 49.3 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 52 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 36.4 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 32 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 35.3 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 29.8 |  | Solo 061331 | 1/3 Oct 6.3kHz | Lin | dB | 28.7
| Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 53.9 | 56.7 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 38.8 | 43.9 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 32.8 | 37.7 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 47.5 | 52.6 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 50.8 | 55.6 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 38.3 | 41.4 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 33 | 36.8 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 34.7 | 39.4 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 31.6 | 35 | Solo 061331 | 1/3 Oct 8kHz | Lin | dB | 35.6 | 36.8
| Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 48.9 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 38.2 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 32.5 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 46.3 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 49.1 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 34.4 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 30.7 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 33.8 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 28.7 |  | Solo 061331 | 1/3 Oct 10kHz | Lin | dB | 26.5
| Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 45.1 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 37.2 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 32.9 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 42.7 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 45.4 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 36.6 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 31.2 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 33.6 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 28.8 |  | Solo 061331 | 1/3 Oct 12.5kHz | Lin | dB | 24.6
| Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 47 | 50.2 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 35.7 | 41.5 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 33.9 | 40.1 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 44.9 | 47.9 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 46.7 | 50.1 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 33.7 | 40.8 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 31.7 | 37.9 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 34.2 | 40.4 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 29.2 | 35.4 | Solo 061331 | 1/3 Oct 16kHz | Lin | dB | 23.1 | 29.7
| Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 43.3 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 37.1 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 37.7 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 41 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 43.3 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 37 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 35.2 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 37.8 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 32.8 |  | Solo 061331 | 1/3 Oct 20kHz | Lin | dB | 26.5

## Existing Upgraded Gas Flare
Current and Previous Gas Flare Locations | Flare Stack Appearance Prior to Upgrade (Current Location) | Previous Flare Stack Detail: |  |  | Previous Gas Flare Specification: |  | Previous Max Flare Noise Level | Upgraded Flare Specification: |  | Key Data for Noise Assessment |  | Key Data for Noise Assessment | Measured Octave band Data for the Existing Flare (WSP Survey 2022)
[11 empty] | Landfill Systems Contact Details | [5 empty] | Lp - Octave Band Sound Pressure Levels - LINEAR
|  |  | (m) | m3/h |  |  | Scroll Down |  |  | Scroll Down | Mobile: +44(0)7850414075 |  | Measurement Ref | Source | Side | Distance (m) | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LAeq,T | LWA | Notes
|  | diameter | 1.12 | - | [6 empty] | Director |  | 6 | Flare Stack | Front | 2 | 83.2 | 76.2 | 67.7 | 72.6 | 64.6 | 61.5 | 51.3 | 49.5 | 41.4 | 40.8 | 68.1 | 82.1206
|  | height | 6.84 | - | [6 empty] | Landfill Systems |  | 7 | Flare Stack | Front | 5 | 80.4 | 72.6 | 66.7 | 64.9 | 57.3 | 54.3 | 47.6 | 44.7 | 36.8 | 37.9 | 60.6 | 82.5794
|  | Min - Max Capaicty | - | 100-500 | [6 empty] | www.lanfill Systems.co.uk |  | 8 | Flare Stack | Left | 5 | 83.4 | 73.8 | 69.3 | 64.7 | 60.2 | 54.9 | 50.4 | 46.6 | 39.4 | 40.4 | 62 | 83.9794 | Use for Flare (highest of individual measurements)
[11 empty] | Landfill Systems, Crowcroft Road Industrial Estate, Nedging with Naughton, Ipswich IP7 7HR |  | 9 | Flare Stack | Right | 2 | 79.3 | 73.4 | 66.6 | 64.2 | 59.3 | 55 | 45.7 | 41.2 | 35 | 35.4 | 61.2 | 75.2206
|  | Upgraded Flare Stack Detail: | [8 empty] | Telephone: +44 (0)1449 744475
|  | diameter | 1.37 | - | [6 empty] | nick@landfillsystems.co.uk |  | Octave Band Sound Power Level
|  | height | 7.48 | - | [8 empty] | Sound Power Level (LW = Sound Pressure Level (Lp) +20*(log(r))+8) |  |  |  | Lw - Octave Band Sound Power Levels - LINEAR
|  | Min - Max Capaicty | - | 200-1000 | [6 empty] | Supplier Discussions: |  |  |  |  | Model Sound Level Library ID | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LW | LWA | Notes
[11 empty] | T-Conv, 19 Nov 2021, 09:35 |  | Data incorported into Noise Model |  |  | F1 | 105.3794 | 95.7794 | 91.2794 | 86.6794 | 82.1794 | 76.8794 | 72.3794 | 68.5794 | 61.3794 | 62.3794 | 106.1 | 83.9794 | From Meas Ref. 7 (worst case)
[11 empty] | Nick Palmer: Landfill Systems do not hold octave band data for the proposed gas flare upgrade or similar systems. | Measure Gas Flare as upgraded and now installed to obtain 1/1 or 1/3 octave band spectra and noise emission levels.
Nick Palmer: the 70dB(A) at 10m is worst case and expected to be lower. Gas Flare noise is rarely an issue in their experience so not necessary for them to hold noise source data
Nick Palmer: Existing Gas Flare is somewhat of a hybrid system, so would be best to measure directly to obtain the required octave band data
[9 empty] | ------> | Maximum Noise Emission Level:
70dB(A) @ 10m
[6 empty] | ------> | Maximum Noise Emission Level:
72dB(A) @ 1m
Current Flare Location
Original Flare Location

## Existing Generator
Measured Octave band Data for the Existing Generator (WSP Survey 2022)
Lp - Octave Band Sound Pressure Levels - LINEAR
Measurement Ref | Source | Side | Distance (m) | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LAeq,T | LWA | Notes
2 | Generator | - | 5 | 77.5 | 71.8 | 78.6 | 72 | 68 | 59.7 | 56.5 | 51.6 | 43.9 | 41.5 | 68.9 | 90.8794 | Generator in issolation
Octave Band Sound Power Level
Sound Power Level (LW = Sound Pressure Level (Lp) +20*(log(r))+8) |  |  |  | Lw - Octave Band Sound Power Levels - LINEAR
|  |  | Model Sound Level Library ID | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LW | LWA | Notes
Data incorported into Noise Model |  |  | G1 | 99.4794 | 93.7794 | 100.5794 | 93.9794 | 89.9794 | 81.6794 | 78.4794 | 73.5794 | 65.8794 | 63.4794 | 104.2 | 90.8794 | From Meas Ref. 2 (Generator in issolation)

## Existing Compressor
Measured Octave band Data for the Existing Compressor (WSP Survey 2022)
Lp - Octave Band Sound Pressure Levels - LINEAR
Measurement Ref | Source | Side | Distance (m) | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LAeq,T | LWA | Notes
1 | Compressor | Right | 2 | 67.7 | 71 | 68.2 | 67.5 | 64 | 64.9 | 60.8 | 61.5 | 56.7 | 50.2 | 69.6 | 83.6206 | Generator in issolation
Octave Band Sound Power Level
Sound Power Level (LW = Sound Pressure Level (Lp) +20*(log(r))+8) |  |  |  | Lw - Octave Band Sound Power Levels - LINEAR
|  |  | Model Sound Level Library ID | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LW | LWA | Notes
Data incorported into Noise Model |  |  | G1 | 81.7206 | 85.0206 | 82.2206 | 81.5206 | 78.0206 | 78.9206 | 74.8206 | 75.5206 | 70.7206 | 64.2206 | 90 | 83.6206 | From Meas Ref. 2 (Generator in issolation)

## Proposed Gas Engine
Manufacturers Data for Propsoed Landfill Gas Powered Engines
Scania SGI-13 (190kW) (Candidate Landfill Gas Powered Electricity Generator for Installation) | Noise Emission Level without Acoustic Enclosure |  | Noise Emission Data with Acoustic Encolsure | Key Data for Noise Assessment |  | Sample Spectral Data for Equivalent Diesel Generator |  | Key Data for Noise Assessment
| Scroll Down | [6 empty] | Scroll Down |  | Example Sound Power Spectra
Lw - Octave Band Sound Power Levels - A-weighted
[11 empty] | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LWA |  | Notes
[11 empty] | - | 84 | 94 | 93 | 96 | 98 | 97 | 93 | 87 | - | 103.5 |  | For Cummins Diesel 250DQDAA Genny in Acoustic Encoslure
Candidate Engine Sound Pressure Level (Lp):
[10 empty] | Lp (dB(A)) | Distance
[10 empty] | 65 | 10
Candidate Engine Sound Power Level (Lw):
Sound Power Level (LW = Sound Pressure Level (Lp) +20*(log(r))+8)
LWA (dB(A))
93
[5 empty] | Maximum Noise Emission Level: |  |  |  |  | Applying octave band Spectra to 93dB(A) LWA.
|  |  |  | ------> | 65dB(A) @ 10m
[5 empty] | WITH ENCLOSURE | [5 empty] | Lw - Octave Band Sound Power Levels - A-weighted - Level adjusted to 93dB LWA
[10 empty] | Difference between LWA Spectra and Candidate LWA | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LWA
[10 empty] | 10.5 | - | 73.5 | 83.5 | 82.5 | 85.5 | 87.5 | 86.5 | 82.5 | 76.5 | - | 93
A-weighting curve
[11 empty] | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz
[11 empty] | -39.4 | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | -6.6
Lw - Octave Band Sound Power Levels - LINEAR - Level adjusted to 93dB LWA
[10 empty] | Model Sound Level Library ID | 31.5Hz | 63Hz | 125Hz | 250Hz | 500Hz | 1kHz | 2kHz | 4kHz | 8kHz | 16kHz | LW | LWA
[9 empty] | Data incorported into Noise Model | G5 | 99.7 | 99.7 | 99.6 | 91.1 | 88.7 | 87.5 | 85.3 | 81.5 | 77.6 | - | 104.9 | 93
Italics = assumed
[7 empty] | ------> | Sample frequency spetra with equiavalent enclosure
Maximum Noise Emission Level:
| ------> | 106dB(A) @ 1m
WITHOUT ENCLOSURE

## Modelled Receptor Results
Summary of Modelled Receptor Noise Levels |  |  |  |  | PASTED RAW MODEL RESULTS
Scenario | Scenario 1 |  | Scenario 2 |  | Model Name | Sandsfield Scenario 1_1.5 | [13 empty] | Model Name | Sandsfield Scenario 2_1.5
Receptor Height | 1.5m | 4.0m | 1.5m | 4.0m | Receptor Height | 1.5 | (daytime) | [12 empty] | Receptor Height | 1.5 | (daytime)
R1 Waterside Edge Caravan Park | 21 | 23 | 23 | 24 | RESULTS: | [14 empty] | RESULTS:
R2 Shooting Range Dwelling | 24 | 25 | 27 | 27 | Name | M. | ID | Level Lr |  | Limit. Value |  | Land Use |  |  | Height |  | Coordinates |  |  | Name | M. | ID | Level Lr |  | Limit. Value |  | Land Use |  |  | Height |  | Coordinates
R3 Catwick Lane 1 | 17 | 19 | 19 | 21 |  |  |  | Day | Night | Day | Night | Type | Auto | Noise Type |  |  | X | Y | Z |  |  |  | Day | Night | Day | Night | Type | Auto | Noise Type |  |  | X | Y | Z
R4 Catwick Lane 2 | 14 | 17 | 15 | 17 |  |  |  | (dBA) | (dBA) | (dBA) | (dBA) |  |  |  | (m) |  | (m) | (m) | (m) |  |  |  | (dBA) | (dBA) | (dBA) | (dBA) |  |  |  | (m) |  | (m) | (m) | (m)
R5 Catwick Lane 3 | 11 | 13 | 15 | 16 | Meas Loc A | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512793 | 446981 | 8.3 | Meas Loc A | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512793 | 446981 | 8.3
R6 Manor Farm | 7 | 10 | 10 | 11 | Meas Loc B | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513087 | 446888 | 13.3 | Meas Loc B | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513087 | 446888 | 13.3
R7 Catfoposs Cottages | 9 | 11 | 11 | 12 | Meas Loc C | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514169 | 447212 | 17.99 | Meas Loc C | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514169 | 447212 | 17.99
R8 Grange House (Catfoss) | 4 | 7 | 7 | 8 | Meas Loc D | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514303 | 446925 | 15.5 | Meas Loc D | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514303 | 446925 | 15.5
R9 Four Acres (Catfoss) | 3 | 6 | 4 | 7 | Meas Loc E | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513092 | 446377 | 11.11 | Meas Loc E | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513092 | 446377 | 11.11
Bold results = highest levels in range of directions |  |  |  |  | The Bungalows | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512408.15 | 447538.78 | 12.5 | The Bungalows | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512408.15 | 447538.78 | 12.5
[5 empty] | R1 Waterside Edge Caravan Park |  | R1 Waterside Edge Caravan Park | 21.3 | 21.3 | 0 | 0 |  | x | Total | 1.5 | r | 512887.3 | 446897.62 | 8.73 | R1 Waterside Edge Caravan Park |  | R1 Waterside Edge Caravan Park | 23.4 | 23.4 | 0 | 0 |  | x | Total | 1.5 | r | 512887.3 | 446897.62 | 8.73
[5 empty] | R2 Shooting Range Dwelling |  | R2 Shooting Range Dwelling | 23.8 | 23.8 | 0 | 0 |  | x | Total | 1.5 | r | 513052.44 | 446927.99 | 9 | R2 Shooting Range Dwelling |  | R2 Shooting Range Dwelling | 26.5 | 26.5 | 0 | 0 |  | x | Total | 1.5 | r | 513052.44 | 446927.99 | 9
BU |  |  |  |  | R3 Catwick Lane 1 |  | R3 Catwick Lane 1 | 17.1 | 17.1 | 0 | 0 |  | x | Total | 1.5 | r | 512872.97 | 446619.27 | 8.6 | R3 Catwick Lane 1 |  | R3 Catwick Lane 1 | 19.1 | 19.1 | 0 | 0 |  | x | Total | 1.5 | r | 512872.97 | 446619.27 | 8.6
Scenario 1 and Scenario 2 similar results |  |  |  |  | R4 Catwick Lane 2 |  | R4 Catwick Lane 2 | 14 | 14 | 0 | 0 |  | x | Total | 1.5 | r | 512907.02 | 446590.33 | 9.55 | R4 Catwick Lane 2 |  | R4 Catwick Lane 2 | 14.9 | 14.9 | 0 | 0 |  | x | Total | 1.5 | r | 512907.02 | 446590.33 | 9.55
Scenario 2 slightly higher levels at some receptors |  |  |  |  | R5 Catwick Lane 3 |  | R5 Catwick Lane 3 | 10.9 | 10.9 | 0 | 0 |  | x | Total | 1.5 | r | 513100.69 | 446364.1 | 10.86 | R5 Catwick Lane 3 |  | R5 Catwick Lane 3 | 14.5 | 14.5 | 0 | 0 |  | x | Total | 1.5 | r | 513100.69 | 446364.1 | 10.86
All receptor results are low levels |  |  |  |  | R6 Manor Farm |  | R6 Manor Farm | 6.9 | 6.9 | 0 | 0 |  | x | Total | 1.5 | r | 514234.59 | 446970.56 | 18.28 | R6 Manor Farm |  | R6 Manor Farm | 9.6 | 9.6 | 0 | 0 |  | x | Total | 1.5 | r | 514234.59 | 446970.56 | 18.28
[5 empty] | R7 Catfoposs Cottages |  | R7 Catfoposs Cottages | 9 | 9 | 0 | 0 |  | x | Total | 1.5 | r | 514184.59 | 447230.24 | 18.5 | R7 Catfoposs Cottages |  | R7 Catfoposs Cottages | 11.1 | 11.1 | 0 | 0 |  | x | Total | 1.5 | r | 514184.59 | 447230.24 | 18.5
[5 empty] | R8 Grange House (Catfoss) |  | R8 Grange House (Catfoss) | 4.1 | 4.1 | 0 | 0 |  | x | Total | 1.5 | r | 514438.9 | 448223.7 | 15.42 | R8 Grange House (Catfoss) |  | R8 Grange House (Catfoss) | 6.6 | 6.6 | 0 | 0 |  | x | Total | 1.5 | r | 514438.9 | 448223.7 | 15.42
[5 empty] | R9 Four Acres (Catfoss) |  | R9 Four Acres (Catfoss) | 3.4 | 3.4 | 0 | 0 |  | x | Total | 1.5 | r | 514023.03 | 448472.3 | 14.91 | R9 Four Acres (Catfoss) |  | R9 Four Acres (Catfoss) | 4.4 | 4.4 | 0 | 0 |  | x | Total | 1.5 | r | 514023.03 | 448472.3 | 14.91
[5 empty] | Model Name | Sandsfield Scenario 1_4 | [13 empty] | Model Name | Sandsfield Scenario 2_4
[5 empty] | Receptor Height | 4 | (night-time) | [12 empty] | Receptor Height | 4 | (night-time)
[5 empty] | RESULTS: | [14 empty] | RESULTS:
[5 empty] | Name | M. | ID | Level Lr |  | Limit. Value |  | Land Use |  |  | Height |  | Coordinates |  |  | Name | M. | ID | Level Lr |  | Limit. Value |  | Land Use |  |  | Height |  | Coordinates
[8 empty] | Day | Night | Day | Night | Type | Auto | Noise Type |  |  | X | Y | Z |  |  |  | Day | Night | Day | Night | Type | Auto | Noise Type |  |  | X | Y | Z
[8 empty] | (dBA) | (dBA) | (dBA) | (dBA) |  |  |  | (m) |  | (m) | (m) | (m) |  |  |  | (dBA) | (dBA) | (dBA) | (dBA) |  |  |  | (m) |  | (m) | (m) | (m)
[5 empty] | Meas Loc A | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512793 | 446981 | 8.3 | Meas Loc A | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512793 | 446981 | 8.3
[5 empty] | Meas Loc B | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513087 | 446888 | 13.3 | Meas Loc B | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513087 | 446888 | 13.3
[5 empty] | Meas Loc C | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514169 | 447212 | 17.99 | Meas Loc C | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514169 | 447212 | 17.99
[5 empty] | Meas Loc D | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514303 | 446925 | 15.5 | Meas Loc D | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 514303 | 446925 | 15.5
[5 empty] | Meas Loc E | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513092 | 446377 | 11.11 | Meas Loc E | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 513092 | 446377 | 11.11
[5 empty] | The Bungalows | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512408.15 | 447538.78 | 12.5 | The Bungalows | - |  | -88 | -88 | 0 | 0 |  | x | Total | 1.5 | r | 512408.15 | 447538.78 | 12.5
[5 empty] | R1 Waterside Edge Caravan Park |  | R1 Waterside Edge Caravan Park | 23 | 23 | 0 | 0 |  | x | Total | 4 | r | 512887.3 | 446897.62 | 11.23 | R1 Waterside Edge Caravan Park |  | R1 Waterside Edge Caravan Park | 24.1 | 24.1 | 0 | 0 |  | x | Total | 4 | r | 512887.3 | 446897.62 | 11.23
[5 empty] | R2 Shooting Range Dwelling |  | R2 Shooting Range Dwelling | 24.9 | 24.9 | 0 | 0 |  | x | Total | 4 | r | 513052.44 | 446927.99 | 11.5 | R2 Shooting Range Dwelling |  | R2 Shooting Range Dwelling | 26.9 | 26.9 | 0 | 0 |  | x | Total | 4 | r | 513052.44 | 446927.99 | 11.5
[5 empty] | R3 Catwick Lane 1 |  | R3 Catwick Lane 1 | 19 | 19 | 0 | 0 |  | x | Total | 4 | r | 512872.97 | 446619.27 | 11.1 | R3 Catwick Lane 1 |  | R3 Catwick Lane 1 | 20.9 | 20.9 | 0 | 0 |  | x | Total | 4 | r | 512872.97 | 446619.27 | 11.1
[5 empty] | R4 Catwick Lane 2 |  | R4 Catwick Lane 2 | 16.7 | 16.7 | 0 | 0 |  | x | Total | 4 | r | 512907.02 | 446590.33 | 12.05 | R4 Catwick Lane 2 |  | R4 Catwick Lane 2 | 17.2 | 17.2 | 0 | 0 |  | x | Total | 4 | r | 512907.02 | 446590.33 | 12.05
[5 empty] | R5 Catwick Lane 3 |  | R5 Catwick Lane 3 | 13.3 | 13.3 | 0 | 0 |  | x | Total | 4 | r | 513100.69 | 446364.1 | 13.36 | R5 Catwick Lane 3 |  | R5 Catwick Lane 3 | 15.6 | 15.6 | 0 | 0 |  | x | Total | 4 | r | 513100.69 | 446364.1 | 13.36
[5 empty] | R6 Manor Farm |  | R6 Manor Farm | 10 | 10 | 0 | 0 |  | x | Total | 4 | r | 514234.59 | 446970.56 | 20.78 | R6 Manor Farm |  | R6 Manor Farm | 11 | 11 | 0 | 0 |  | x | Total | 4 | r | 514234.59 | 446970.56 | 20.78
[5 empty] | R7 Catfoposs Cottages |  | R7 Catfoposs Cottages | 10.8 | 10.8 | 0 | 0 |  | x | Total | 4 | r | 514184.59 | 447230.24 | 21 | R7 Catfoposs Cottages |  | R7 Catfoposs Cottages | 11.7 | 11.7 | 0 | 0 |  | x | Total | 4 | r | 514184.59 | 447230.24 | 21
[5 empty] | R8 Grange House (Catfoss) |  | R8 Grange House (Catfoss) | 7.2 | 7.2 | 0 | 0 |  | x | Total | 4 | r | 514438.9 | 448223.7 | 17.92 | R8 Grange House (Catfoss) |  | R8 Grange House (Catfoss) | 7.6 | 7.6 | 0 | 0 |  | x | Total | 4 | r | 514438.9 | 448223.7 | 17.92
[5 empty] | R9 Four Acres (Catfoss) |  | R9 Four Acres (Catfoss) | 6 | 6 | 0 | 0 |  | x | Total | 4 | r | 514023.03 | 448472.3 | 17.41 | R9 Four Acres (Catfoss) |  | R9 Four Acres (Catfoss) | 7 | 7 | 0 | 0 |  | x | Total | 4 | r | 514023.03 | 448472.3 | 17.41